# Appendix C: Landfill Gas Management Technology Comparison

## C.1 Introduction

This appendix provides a comprehensive comparison of available technologies for managing landfill gas at sites with declining gas generation, such as Stormy West Landfill. The comparison includes technical specifications, operational characteristics, costs, and suitability for different gas quality conditions.

## C.2 Technology Categories

Landfill gas management technologies can be categorized into three main groups:

Active Combustion Systems: Flares and thermal oxidizers that actively destroy methane through high-temperature combustion

Energy Recovery Systems: Technologies that utilize landfill gas for energy generation

Passive Treatment Systems: Biological systems that oxidize methane through microbial activity

## C.3 Active Combustion Systems

### C.3.1 Conventional High-Temperature Flares

Description:

Conventional flares are designed to combust landfill gas at temperatures of 1,000-1,200°C with retention times of 0.3-0.6 seconds to ensure complete destruction of methane and other volatile organic compounds.

Technical Specifications:

| Parameter | Typical Range |
| --- | --- |
| Capacity | 100-2,000 m³/hr |
| Methane Range | 30-60% by volume |
| Minimum Flow | 50-100 m³/hr |
| Destruction Efficiency | >98% for CH₄ |
| Operating Temperature | 1,000-1,200°C |
| Retention Time | 0.3-0.6 seconds |
| Power Requirement | 5-15 kW |

Advantages:

Proven technology with extensive track record

High destruction efficiency

Reliable operation

Meets regulatory requirements

Multiple suppliers available

Lower capital cost compared to specialized systems

Disadvantages:

Requires minimum methane concentration (typically >30%)

Not suitable for declining gas quality

May require supplementary fuel at low CH₄ concentrations

Higher operational costs at low gas flows

Limited turndown capability

Typical Applications:

Active landfills with high gas generation

Sites with methane concentrations >30%

Large-scale gas management systems

Cost Estimates:

| Cost Component | Range (£) |
| --- | --- |
| Capital Cost | £80,000 - £150,000 |
| Installation | £20,000 - £40,000 |
| Annual Operating Cost | £15,000 - £25,000 |
| Maintenance (Annual) | £5,000 - £10,000 |
| Lifespan | 15-20 years |

### C.3.2 Low-CV (Low Calorific Value) Flares

Description:

Low-CV flares are specifically designed to combust landfill gas with low methane concentrations (10-30%) through optimized burner design and enhanced air/gas mixing systems.

Technical Specifications:

| Parameter | Typical Range |
| --- | --- |
| Capacity | 40-500 m³/hr |
| Methane Range | 10-30% by volume |
| Minimum Flow | 20-40 m³/hr |
| Destruction Efficiency | >98% for CH₄ |
| Operating Temperature | 1,000-1,200°C |
| Retention Time | 0.3-0.6 seconds |
| Turndown Ratio | 3:1 to 5:1 |
| Power Requirement | 3-10 kW |

Advantages:

Designed for low methane concentrations

Wide operating range (10-30% CH₄)

High turndown capability

Automated operation with remote monitoring

Suitable for declining gas generation

No supplementary fuel required in normal operation

Meets regulatory temperature and retention requirements

Disadvantages:

Higher capital cost than conventional flares

More complex burner design

Requires specialized maintenance

Limited number of suppliers

May still require batch operation at very low flows

Typical Applications:

Closed landfills with declining gas generation

Sites with methane concentrations 10-30%

Batch burning operations

Transition from active to passive management

Cost Estimates:

| Cost Component | Range (£) |
| --- | --- |
| Capital Cost | £120,000 - £200,000 |
| Installation | £25,000 - £45,000 |
| Annual Operating Cost | £12,000 - £20,000 |
| Maintenance (Annual) | £6,000 - £12,000 |
| Lifespan | 15-20 years |

Recommended Suppliers:

Landfill Systems (UK) - LS-LCV Series

Organics (UK) - Low-CV Flare Range

Hofstetter (Switzerland) - LCV-Flare Series

LFG Technologies (US) - Low-BTU Flare Systems

### C.3.3 Catalytic Oxidizers

Description:

Catalytic oxidizers use precious metal catalysts to oxidize methane at lower temperatures (350-500°C) compared to thermal oxidizers.

Technical Specifications:

| Parameter | Typical Range |
| --- | --- |
| Capacity | 50-1,000 m³/hr |
| Methane Range | 5-25% by volume |
| Operating Temperature | 350-500°C |
| Destruction Efficiency | >95% for CH₄ |
| Catalyst Type | Platinum/Palladium |
| Catalyst Life | 3-5 years |
| Power Requirement | 10-25 kW |

Advantages:

Lower operating temperature

Can handle very low methane concentrations

Lower energy consumption

Reduced NOx emissions

Quiet operation

Disadvantages:

High capital cost

Catalyst poisoning by siloxanes and other contaminants

Regular catalyst replacement required

Sensitive to gas composition variations

Pre-treatment may be required

Limited application in UK landfills

Typical Applications:

Sites with very low methane concentrations

Applications requiring low emissions

Indoor installations

Cost Estimates:

| Cost Component | Range (£) |
| --- | --- |
| Capital Cost | £150,000 - £250,000 |
| Installation | £30,000 - £50,000 |
| Annual Operating Cost | £20,000 - £35,000 |
| Catalyst Replacement | £15,000 - £25,000 (every 3-5 years) |
| Lifespan | 15-20 years |

## C.4 Energy Recovery Systems

### C.4.1 Gas Engines (Electricity Generation)

Description:

Gas engines convert landfill gas chemical energy into electricity through internal combustion.

Technical Specifications:

| Parameter | Typical Range |
| --- | --- |
| Capacity | 100-3,000 kWe |
| Methane Requirement | >35% by volume |
| Minimum Flow | 200-500 m³/hr |
| Electrical Efficiency | 35-42% |
| Overall Efficiency (CHP) | 75-85% |
| Maintenance Interval | 1,000-2,000 hours |

Advantages:

Revenue generation from electricity sales

High overall efficiency with CHP

Proven technology

Can provide on-site power

Disadvantages:

Requires high methane concentration (>35%)

High capital cost

Intensive maintenance requirements

Not suitable for declining gas generation

Requires minimum flow rates

Complex permitting requirements

Suitability for Stormy West:

NOT SUITABLE - Current methane concentrations (20.93%) are below minimum requirements, and declining gas generation makes this option unviable.

### C.4.2 Gas Turbines

Description:

Gas turbines convert landfill gas energy into electricity through combustion and expansion.

Technical Specifications:

| Parameter | Typical Range |
| --- | --- |
| Capacity | 500-5,000 kWe |
| Methane Requirement | >40% by volume |
| Minimum Flow | 500-2,000 m³/hr |
| Electrical Efficiency | 25-35% |
| Maintenance Interval | 2,000-4,000 hours |

Advantages:

High capacity

Lower maintenance than engines

Compact design

Disadvantages:

Very high capital cost

Requires very high methane concentration

Not suitable for small sites

Requires minimum flow rates

Suitability for Stormy West:

NOT SUITABLE - Gas quality and quantity far below minimum requirements.

## C.5 Passive Treatment Systems

### C.5.1 Biofilters

Description:

Biofilters are engineered systems consisting of a porous material layer and an organic material (typically compost) layer that oxidizes methane through biological activity.

Technical Specifications:

| Parameter | Typical Range |
| --- | --- |
| Methane Oxidation Rate | 50-90% |
| Optimal CH₄ Concentration | 5-25% by volume |
| Loading Rate | 5-50 g CH₄/m²/day |
| Media Depth | 0.5-1.5 m |
| Media Type | Compost, soil, or mixed media |
| Moisture Content | 40-60% |
| Temperature Range | 10-40°C |

Design Considerations:

Media Selection:

Mature compost (preferred)

Soil/compost mixtures

Engineered media with specific properties

Particle size: 10-50 mm

System Configuration:

Passive (no forced air)

Active (with air injection)

Horizontal or vertical flow

Area Requirements:

Typical loading: 20-30 g CH₄/m²/day

For 180 m³/hr at 20% CH₄: approximately 1,000-1,500 m² required

Advantages:

Low operational costs

No energy requirement (passive systems)

No secondary air pollutant emissions

Can handle variable gas flows

Suitable for very low methane concentrations

Natural appearance

Can be integrated into site landscaping

Disadvantages:

Large land area required

Variable performance depending on environmental conditions

Seasonal variations in oxidation rates

May not meet Landfill Directive flaring requirements

Requires regular maintenance (moisture management)

Limited commercial applications in UK

Performance monitoring challenging

May require regulatory approval/exemption

Typical Applications:

Closed landfills with very low gas generation

Sites with methane concentrations <15%

Supplementary treatment for flare systems

Final stage of gas management

Cost Estimates:

| Cost Component | Range (£) |
| --- | --- |
| Capital Cost | £50,000 - £100,000 |
| Installation | £30,000 - £60,000 |
| Annual Operating Cost | £3,000 - £8,000 |
| Media Replacement | £10,000 - £20,000 (every 5-7 years) |
| Lifespan | 20-30 years |

Performance Factors:

| Factor | Impact on Performance |
| --- | --- |
| Temperature | Optimal: 20-30°C; Reduced below 10°C |
| Moisture | Critical: 40-60% optimal; <30% or >70% reduces efficiency |
| CH₄ Concentration | Optimal: 5-15%; Reduced above 25% |
| Loading Rate | Optimal: 20-30 g/m²/day; Overloading reduces efficiency |
| Media Age | Decreases over time; replacement needed every 5-7 years |

### C.5.2 Biocovers

Description:

Biocovers are passive systems where a porous material layer is laid directly on top of the landfill surface, covered by an oxidizing layer of mature compost.

Technical Specifications:

| Parameter | Typical Range |
| --- | --- |
| Methane Oxidation Rate | 40-80% |
| Optimal CH₄ Concentration | 5-20% by volume |
| Cover Thickness | 0.3-1.0 m |
| Media Type | Compost or compost/soil mixture |
| Application Area | Entire landfill surface or targeted areas |

Advantages:

Very low operational costs

Minimal infrastructure required

Can be applied over large areas

Integrates with final cover

Natural appearance

No energy requirement

Disadvantages:

Lower oxidation efficiency than biofilters

Highly dependent on environmental conditions

Difficult to monitor performance

May not meet regulatory requirements

Requires suitable climate conditions

Limited UK experience

Typical Applications:

Final stage of gas management

Sites with very low gas generation

Supplementary to active systems

Areas with diffuse emissions

Cost Estimates:

| Cost Component | Range (£) |
| --- | --- |
| Capital Cost | £30,000 - £60,000 |
| Installation | £20,000 - £40,000 |
| Annual Operating Cost | £2,000 - £5,000 |
| Media Replacement | £15,000 - £30,000 (every 7-10 years) |
| Lifespan | 20-30 years |

### C.5.3 Passive Venting

Description:

Passive venting allows landfill gas to escape through engineered vents without active extraction or treatment.

Suitability for Stormy West:

NOT RECOMMENDED - Does not meet regulatory requirements for methane destruction and would result in uncontrolled greenhouse gas emissions.

## C.6 Comparative Analysis

### C.6.1 Technical Comparison Matrix

| Technology | CH₄ Range (%) | Flow Range (m³/hr) | Destruction Efficiency | Complexity | Suitability for Stormy West |
| --- | --- | --- | --- | --- | --- |
| Conventional Flare | 30-60 | 100-2,000 | >98% | Low | Poor - CH₄ too low |
| Low-CV Flare | 10-30 | 40-500 | >98% | Medium | **Excellent** |
| Catalytic Oxidizer | 5-25 | 50-1,000 | >95% | High | Good - but higher cost |
| Gas Engine | >35 | 200-3,000 | N/A | High | Not suitable |
| Biofilter | 5-25 | Variable | 50-90% | Medium | Future option |
| Biocover | 5-20 | Variable | 40-80% | Low | Future option |

### C.6.2 Cost Comparison

Total Cost of Ownership (10-year period):

| Technology | Capital + Installation | Operating (10 years) | Total 10-Year Cost |
| --- | --- | --- | --- |
| Conventional Flare | £120,000 | £200,000 | £320,000 |
| Low-CV Flare | £165,000 | £160,000 | £325,000 |
| Catalytic Oxidizer | £200,000 | £350,000 | £550,000 |
| Biofilter | £80,000 | £50,000 | £130,000 |
| Biocover | £50,000 | £30,000 | £80,000 |

Note: Biofilter and biocover costs assume regulatory approval for use without active flaring.

### C.6.3 Environmental Performance Comparison

| Technology | CH₄ Destruction | CO₂ Equivalent Reduction | NOx Emissions | Noise Level |
| --- | --- | --- | --- | --- |
| Conventional Flare | >98% | High | Moderate | Moderate |
| Low-CV Flare | >98% | High | Moderate | Moderate |
| Catalytic Oxidizer | >95% | High | Low | Low |
| Biofilter | 50-90% | Moderate-High | None | None |
| Biocover | 40-80% | Moderate | None | None |

### C.6.4 Operational Comparison

| Technology | Automation Level | Maintenance Frequency | Skill Level Required | Reliability |
| --- | --- | --- | --- | --- |
| Conventional Flare | High | Quarterly | Medium | High |
| Low-CV Flare | High | Quarterly | Medium | High |
| Catalytic Oxidizer | High | Monthly | High | Medium |
| Biofilter | Low | Monthly | Low | Medium |
| Biocover | None | Quarterly | Low | Medium |

## C.7 Regulatory Compliance Assessment

### C.7.1 Landfill Directive Requirements

The EU Landfill Directive (1999/31/EC) requires that landfill gas must be collected and:

Used to produce energy, or

Flared, or

Treated in some other way if energy production is not economically viable

Compliance Assessment:

| Technology | Meets Directive | Comments |
| --- | --- | --- |
| Conventional Flare | Yes | Fully compliant |
| Low-CV Flare | Yes | Fully compliant |
| Catalytic Oxidizer | Yes | Fully compliant |
| Biofilter | Uncertain | May require regulatory approval/exemption |
| Biocover | Uncertain | May require regulatory approval/exemption |

### C.7.2 Environmental Permit Requirements

The site's Environmental Permit (EAWML34009) requires:

Effective gas management to prevent environmental harm

Monitoring and reporting of gas management system performance

Compliance with emission limits

All active combustion systems meet these requirements. Passive systems may require permit variation.

## C.8 Technology Selection Criteria

### C.8.1 Short-Term Requirements (1-2 years)

Priority Criteria:

Ability to handle current gas quality (20% CH₄)

Regulatory compliance

Reliability

Reasonable capital cost

Recommended Technology: Low-CV Flare

Justification:

Specifically designed for current gas quality

Meets all regulatory requirements

Proven technology with multiple suppliers

Reasonable total cost of ownership

Can accommodate declining gas generation

### C.8.2 Medium-Term Requirements (3-5 years)

Priority Criteria:

Ability to handle declining gas quality (15-20% CH₄)

Lower operational costs

Flexibility for future changes

Environmental performance

Recommended Technology: Low-CV Flare with pilot biofilter testing

Justification:

Low-CV flare continues to meet requirements

Pilot biofilter provides data for future transition

Maintains regulatory compliance

Prepares for eventual passive management

### C.8.3 Long-Term Requirements (5+ years)

Priority Criteria:

Ability to handle very low gas quality (<15% CH₄)

Minimal operational costs

Passive operation

Environmental sustainability

Recommended Technology: Biofilter or biocover (subject to regulatory approval)

Justification:

Suitable for very low gas concentrations

Minimal operational costs

Sustainable long-term solution

Natural integration with site restoration

## C.9 Implementation Recommendations

### C.9.1 Phased Approach

Phase 1 (Years 1-2): Low-CV Flare Installation

Replace current flare with low-CV system

Optimize gas collection system

Establish baseline performance

Phase 2 (Years 3-5): Pilot Testing

Install pilot biofilter in selected area

Monitor performance over multiple seasons

Engage with NRW regarding future passive management

Phase 3 (Years 5+): Transition to Passive Management

Expand biofilter/biocover based on pilot results

Gradually reduce active flaring

Maintain monitoring program

### C.9.2 Risk Mitigation

Technical Risks:

Low-CV flare performance below expectations → Select proven supplier with performance guarantees

Biofilter pilot shows poor performance → Continue with low-CV flare, extend pilot testing

Regulatory approval not granted for passive systems → Continue with active flaring

Financial Risks:

Higher than expected costs → Phased implementation allows budget adjustment

Equipment failure → Select suppliers with strong warranty and support

Regulatory Risks:

Permit variation required → Early engagement with NRW

Compliance issues → Maintain active system as backup

## C.10 Conclusions

Based on the comprehensive technology comparison:

Short-Term Solution: Low-CV flare is the most appropriate technology for immediate implementation at Stormy West Landfill, offering the best balance of technical performance, regulatory compliance, and cost-effectiveness.

Medium-Term Strategy: Continued operation of low-CV flare with pilot testing of biofilter technology to prepare for future transition.

Long-Term Vision: Transition to passive biological treatment (biofilter or biocover) as gas generation continues to decline, subject to regulatory approval and demonstrated performance.

Not Recommended: Conventional flares (insufficient for current gas quality), energy recovery systems (gas quality and quantity insufficient), and passive venting (non-compliant).

This phased approach provides a clear pathway for managing declining gas generation while maintaining regulatory compliance and optimizing costs over the long term.

## C.11 References

Environment Agency. (2004). Guidance on the management of landfill gas. LFTGN 03.

Environment Agency. (2009). Case study: Cheshire County Council's use of low calorific flares on closed historic landfill sites.

U.S. EPA. (2021). Apply Biofilters or Biocovers. Landfill Methane Outreach Program.

Scheutz, C., Kjeldsen, P., Bogner, J.E., et al. (2009). Microbial methane oxidation processes and technologies for mitigation of landfill gas emissions. Waste Management & Research, 27(5), 409-455.

Huber-Humer, M., Gebert, J., and Hilger, H. (2008). Biotic systems to mitigate landfill methane emissions. Waste Management & Research, 26(1), 33-46.

European Commission. (1999). Council Directive 1999/31/EC on the landfill of waste.