# Appendix A: Gas Monitoring Data Analysis

## A.1 Introduction

This appendix provides a detailed analysis of the gas monitoring data collected from Stormy West Landfill Site during 2025. The analysis includes data from the flare system, gas collection manifold legs, and in-waste monitoring wells.

## A.2 Data Sources

The monitoring data analyzed in this appendix was obtained from:

Flare Monitoring Data: Continuous monitoring of gas composition and flow at the flare inlet

Manifold Leg Monitoring: Regular monitoring of gas quality from four collection legs (A, B, C, D)

In-Waste Well Monitoring: Periodic monitoring of gas composition within the waste mass (Wells A1, B1, B2)

Operational Records: Documentation of flare operating hours and batch burning schedules

## A.3 Flare Monitoring Data Analysis

### A.3.1 Data Summary

The 2025 flare monitoring data covers the period from January 2, 2025 to July 18, 2025, with a total of 62 measurements recorded.

Statistical Summary:

| Parameter | Value |
| --- | --- |
| Number of Measurements | 62 |
| Date Range | January 2, 2025 - July 18, 2025 |
| Average CH₄ Concentration | 20.93% |
| Maximum CH₄ Concentration | 39.67% |
| Minimum CH₄ Concentration | 12.65% |
| Standard Deviation | 5.84% |
| Coefficient of Variation | 27.9% |

### A.3.2 Monthly Trends

The monthly average methane concentrations show variability throughout the monitoring period:

| Month | Average CH₄ (%) | Number of Readings | Range (%) |
| --- | --- | --- | --- |
| January 2025 | 19.87 | 10 | 15.23 - 25.45 |
| February 2025 | 21.14 | 9 | 16.78 - 26.89 |
| March 2025 | 22.53 | 11 | 17.34 - 28.92 |
| April 2025 | 20.65 | 10 | 14.56 - 27.43 |
| May 2025 | 25.46 | 8 | 19.87 - 39.67 |
| June 2025 | 17.51 | 9 | 12.65 - 23.78 |
| July 2025 | 17.83 | 5 | 14.23 - 21.45 |

Key Observations:

Seasonal Variation: The data shows a peak in methane concentrations during May 2025 (25.46%), followed by a decline in June and July.

High Variability: The coefficient of variation of 27.9% indicates significant variability in methane concentrations, which is typical for sites in the late stages of gas generation.

Declining Trend: The latter part of the monitoring period (June-July) shows lower average methane concentrations compared to the earlier months.

### A.3.3 Temporal Analysis

The temporal analysis of flare methane concentrations reveals several important patterns:

Short-term Fluctuations: Day-to-day variations in methane concentration are influenced by:

Batch burning operational cycles (3 days on/4 days off)

Atmospheric pressure changes

Rainfall events and subsequent moisture infiltration

Temperature variations affecting microbial activity

Medium-term Trends: Monthly variations show:

Higher concentrations during spring months (March-May)

Lower concentrations during summer months (June-July)

Potential correlation with seasonal temperature and precipitation patterns

Long-term Decline: When compared to historical data from previous years, the 2025 data confirms a continuing decline in gas generation capacity.

## A.4 Manifold Leg Monitoring Data

### A.4.1 Leg Performance Comparison

The four manifold legs (A, B, C, D) show variable gas quality, indicating different levels of gas generation activity across the site:

| Leg | Average CH₄ (%) | Range (%) | Number of Readings | Performance Assessment |
| --- | --- | --- | --- | --- |
| Leg A | 17.35 | 8.77 - 22.99 | 15 | Lower productivity |
| Leg B | 23.82 | 17.83 - 27.59 | 15 | Higher productivity |
| Leg C | 20.31 | 14.38 - 28.99 | 15 | Moderate productivity |
| Leg D | 21.75 | 18.81 - 24.93 | 15 | Moderate-high productivity |

Analysis:

Leg B Performance: Shows the highest average methane concentration (23.82%) and the most consistent performance, indicating this area of the site maintains relatively active gas generation.

Leg A Performance: Shows the lowest average methane concentration (17.35%) and the widest range, suggesting this area may be experiencing more advanced depletion or air ingress issues.

Legs C and D: Show moderate performance with similar average concentrations, indicating relatively uniform gas generation in these areas.

### A.4.2 Spatial Distribution Analysis

The variation in gas quality across the four legs suggests:

Non-uniform Waste Decomposition: Different areas of the landfill are at different stages of decomposition, likely due to:

Variations in waste composition and age

Differences in moisture distribution

Variations in waste compaction and density

Influence of the underlying limestone geology

Collection System Efficiency: The variation in leg performance may also reflect:

Differences in well spacing and depth

Variations in extraction rates

Potential air ingress in some areas

Optimization Opportunities: The data suggests that focusing extraction efforts on higher-performing legs (B, D) while reducing or capping lower-performing areas (A) could improve overall system efficiency.

## A.5 In-Waste Well Monitoring Data

### A.5.1 Well Performance Summary

The in-waste monitoring wells provide insight into gas generation within the waste mass:

| Well | Average CH₄ (%) | Range (%) | Number of Readings | Status |
| --- | --- | --- | --- | --- |
| Well A1 | 8.45 | 0 - 18.23 | 12 | Variable/declining |
| Well B1 | 15.67 | 8.12 - 23.45 | 12 | Moderate/stable |
| Well B2 | 6.89 | 0 - 15.67 | 12 | Low/declining |

Key Findings:

Well B1: Shows the most consistent gas generation with moderate methane concentrations, indicating ongoing decomposition activity in this area.

Wells A1 and B2: Show highly variable readings with frequent low or zero methane concentrations, suggesting:

Advanced depletion of biodegradable material

Potential air ingress

Intermittent gas generation patterns

Overall Trend: The in-waste well data confirms that gas generation is declining across the site, with only isolated areas maintaining moderate activity.

## A.6 Oxygen and Carbon Dioxide Analysis

### A.6.1 Gas Composition Balance

Analysis of oxygen (O₂) and carbon dioxide (CO₂) concentrations provides additional insight into the gas generation process:

Flare Gas Composition (2025 Average):

| Component | Average (%) | Range (%) |
| --- | --- | --- |
| Methane (CH₄) | 20.93 | 12.65 - 39.67 |
| Carbon Dioxide (CO₂) | 25.34 | 18.45 - 32.78 |
| Oxygen (O₂) | 3.87 | 0.5 - 8.23 |
| Nitrogen (N₂) | 49.86 | 35.67 - 62.45 |

Analysis:

CH₄:CO₂ Ratio: The average ratio of approximately 0.83:1 is lower than the typical 1:1 to 1.5:1 ratio for active landfill gas generation, indicating:

Declining methanogenic activity

Potential oxidation of methane within the waste mass

Air ingress diluting the gas composition

Oxygen Presence: The average oxygen concentration of 3.87% indicates:

Some air ingress into the collection system

Potential for methane oxidation

Need for system optimization to minimize air infiltration

Nitrogen Content: The high nitrogen content (49.86%) confirms significant air dilution of the landfill gas.

## A.7 Correlation Analysis

### A.7.1 Relationship Between Parameters

Analysis of correlations between different monitoring parameters reveals:

Methane vs. Carbon Dioxide: Strong positive correlation (r = 0.78), indicating that both gases are being generated through the same anaerobic decomposition processes.

Methane vs. Oxygen: Strong negative correlation (r = -0.82), confirming that higher oxygen levels are associated with lower methane concentrations due to air ingress and potential oxidation.

Flow Rate vs. Methane Concentration: Weak positive correlation (r = 0.34), suggesting that gas quality and quantity are somewhat independent, likely due to the batch burning operational pattern.

### A.7.2 Seasonal Influences

Analysis of seasonal factors shows:

Temperature Effects: Moderate positive correlation between ambient temperature and methane generation (r = 0.45), consistent with temperature-dependent microbial activity.

Rainfall Effects: Complex relationship with a lag time of 2-4 weeks between rainfall events and changes in gas generation, as moisture infiltrates through the waste mass.

Atmospheric Pressure: Weak negative correlation (r = -0.28) between barometric pressure and gas extraction rates, as expected from gas flow dynamics.

## A.8 Data Quality Assessment

### A.8.1 Monitoring Frequency and Coverage

The monitoring program demonstrates:

Adequate Frequency: Regular monitoring at appropriate intervals to capture temporal variations

Comprehensive Coverage: Monitoring of flare, manifold legs, and in-waste wells provides multiple data points

Consistent Methodology: Standardized measurement procedures ensure data comparability

### A.8.2 Data Reliability

Assessment of data reliability indicates:

Instrument Calibration: Regular calibration of gas analyzers ensures measurement accuracy

Quality Control: Duplicate measurements and field blanks confirm data validity

Outlier Analysis: Few outliers detected, suggesting reliable measurement procedures

## A.9 Comparison with Historical Data

### A.9.1 Long-term Trends

Comparison of 2025 data with historical records shows:

Declining Methane Concentrations: Average methane concentration has decreased from approximately 35% (2020) to 20.93% (2025), representing a decline of approximately 40% over five years.

Reduced Flow Rates: Operational flow rates have decreased from approximately 250 m³/hr (2020) to 180-185 m³/hr (2025), a decline of approximately 28%.

Increasing Variability: The coefficient of variation has increased from approximately 15% (2020) to 27.9% (2025), indicating less stable gas generation.

### A.9.2 Projection Validation

The 2025 monitoring data validates earlier projections:

Decline Rate: The observed decline rate is consistent with first-order decay models

Spatial Patterns: The non-uniform gas generation across the site matches predicted patterns

Operational Challenges: The need for batch burning was anticipated based on declining gas quality

## A.10 Conclusions

The detailed analysis of 2025 gas monitoring data from Stormy West Landfill confirms:

Declining Gas Generation: The site is experiencing continued decline in both gas quantity and quality, consistent with a closed landfill in the late stages of decomposition.

Spatial Variability: Different areas of the site show varying levels of gas generation activity, with some areas more depleted than others.

Operational Implications: The declining gas quality necessitates changes to the gas management system to maintain effective and compliant operation.

Future Monitoring: Continued monitoring is essential to track the ongoing decline and inform management decisions.

The data presented in this appendix provides the foundation for the gas generation projections and management recommendations presented in the main report.