## Current asset evaluation
Zone 1 - Cake import silos
Description | Cake import silos
Number of tanks | 2
Volume of tank | 2 x 40m3 Lorries of 15 and 28m3
Material of tank | Steel
Above/below ground? | Below ground - hopper and silo is surrounded by a concrete structure.
Pipe material | Above and below ground - Stainless steel
Drainage for zone | Gullies along front of cake import areas - connected to liquor return tank. Sump pump located in the concrete structure to drain surface water from rainfall.
Year of construction | 2010
Surrounding area | Mostly surrounded with concrete (impermeable) Area of loose stone to the north-west of silo (permeable) Area to the east - bitumen road (impermeable)
Pump rate - import hopper pump | 20m3/hr approximately
Is asset fit for purpose? | The tanks were originally designed and constructed as import cake silos. They have been operating with no notable concerns. Tanks have not undergone a change of use. Fit for purpose
Condition of the tank Any tank failures - cracks, flaking, corrosion, overflows, overfilling? | Hopper area has filled in the past with sludge and cleaned out. Category R - sump Existing leak on sliding frame through the hopper - hole is getting elongated (seepage through hopper)
Condition of pipework Pipe leaks, corrosion? | External corrosion of external pipework due to extremities - general material condition bad Electrical containment and valve gets corroded frequently
Protection of assets - bollards? | Vehicle guardrails
Control/monitoring/alarming measures in place? | Available silo volume indicators - also raises alarms if there is operational issues Indicators are linked to both silos and THP silo level Pressure sensor and alarms >30bar
Secondary containment provided? | Secondary containment provided by concrete structure surrounding imported cake silo.
Secondary containment condition? | Concrete is only 10 years' old and appears to been very good condition based on observation. No intrusive structural inspection has taken place.
04/08/2020
File Ref
Version
B14411-123532-ZZ-XX-AS-ZA-CI1010
P01
Originator
Jacques Calitz
James Croston
Date
Date
30/06/2020
04/08/2020
Checker
Zone 1 (Imported cake silo)
IED CIRIA 736 Risk Assessment
James Croston
Approver
Date

## Risk assessment
Source
Material | Physical properties | Maximum quantity | units | Storage | Flammability | Corrosive | Ecotoxicity (based on LD and quantity) | Hazard rating
Imported cake (silo 1) | Imported cake | 40 (total volume) | m3 | Concrete below ground | Not flammable | Possibly | Organic heavy - Nitrogen, Phosphorous, Ammonia, BOD, TSS, COD - Environmental hazard (algae blooms and death of organisms) Pathogens - Human hazard (E.coli etc.) | M
Imported cake (silo 2) | Imported cake | 40 (total volume) | m3 | Concrete below ground | Not flammable | Possibly | Organic heavy - Nitrogen, Phosphorous, Ammonia, BOD, TSS, COD - Environmental hazard (algae blooms and death of organisms) Pathogens - Human hazard (E.coli etc.) | M
Imported cake (tanker) | Imported cake | 25 | m3 | Lorry/truck - above ground | Not flammable | Possibly | Organic heavy - Nitrogen, Phosphorous, Ammonia, BOD, TSS, COD - Environmental hazard (algae blooms and death of organisms) Pathogens - Human hazard (E.coli etc.) | M
Imported cake (tanker) | Imported cake | 18 | m3 | Lorry/truck - above ground | Not flammable | Possibly | Organic heavy - Nitrogen, Phosphorous, Ammonia, BOD, TSS, COD - Environmental hazard (algae blooms and death of organisms) Pathogens - Human hazard (E.coli etc.) | M
Rainwater run-off contaminated by inventory | Surface water mixed with sludge | Dependent on area of containment | m3 | N/A | Not flammable | No | Lower concentration of sludge contaminants | L
[7 empty] | Overall | M
Pathway and Receptor
Pathway - the route from primary containment to receptor (extent of loss of containment) |  | Time of concentration/ duration of source outside containment |  | Hazard - Transport potential |  |  | Receptor | Hazard - Damage potential
Permeable area/ground (north west of silos) and below concrete surround of cake import area Permeable sub-soils/strata - infiltrates into soil Unlikely to reach the soil (gullies and area doesn’t drain to permeable area) |  | Minutes to hours Due to the type of inventory, cake with 22% DS content, the viscosity of the fluid is low and will not easily cascade downstream or flow out of containment. Most of the loss of containment will be around the import area or within the underground concrete secondary containment. |  | L |  |  | Groundwater (underlain by a secondary aquifer) - contaminated through percolation through soil or through fluctuating tidal groundwater level Over a very long period, could slightly contaminate shoreline through groundwater base flow underground | L
Tidally fluctuating groundwater |  |  |  | L
Existing underground services - ductwork, tunnels etc. |  |  |  | L
There is impermeable tarmac road surfacing north of the tanks. If inventory is cascaded onto road (saturated permeable ground), sludge will be transported downstream along the road surface into the road gullies and into the site drainage system (liquor return) |  |  |  | L |  |  | WWTW - drainage network is connected to liquor return tank returning back to the head of the works (SBR tank) | L
|  | Overall |  | L |  |  | Overall | L
Combination of Hazards | MLL
Overall risk rating for zone (Ciria 736) | L
Frequency of loss of containment
Failure mode | Description | Existing consequence and mitigation measure | [6 empty] | Annual probability of loss of containment | Rating
Operational failure - tanker (partial - catastrophic) | Overtopping of skip/tanker | Filling of silo via 18/25m3 lorries/trucks is done with operational staff present. There has been cake spills within the hopper and silo area (skip overtopping), but that was contained within the secondary concrete containment structure or in the hardstanding area in front of the import cake bays and cleaned. Total loss of containment is unlikely (partial loss of containment would be more likely to occur but would be contained) | [6 empty] | 1 in 100 to 1 in 1 Million | M
Operational failure - tank (partial) | Overfilling/overflow of tank | No known issues with overfilling and overflow. There are level sensors within each of the silos ensuring they are not overfilled. If overfilling occurred, would be contained within the concrete encased containment underground. Total loss of containment is unlikely (partial loss of containment would be more likely to occur but would be contained) | [6 empty] | > 1 in 1 Million | L
Structural failure - tank (catastrophic) | Catastrophic failure due to significant external damage - hopper and import silo | Both the import silo and hopper is located below ground within the a concrete secondary containment structure below ground. In the case of significant damage during operation or maintenance, the total volume contained within the import silo and hopper would be contained within the secondary containment concrete structure and any liquids would drain towards the drainage pump connected to the liquor return. Due to operational presence on site, large drops in levels in the tanks and significant damage (leaks/cracks/corrosion) would be noticed. Total loss of containment of the import silo could occur but the inventory would be contained within concrete underground structure. The silos can easily be taken offline to allow any repairs needed to arrest gradual deterioration. If the concrete encased containment were to fail in conjunction with the hopper/import silo (not deemed to be a credible scenario), the cake liquid could percolate into the permeable soil at a slow rate over a long period. | [6 empty] | > 1 in 1 Million | L
Structural failure - tank (partial) | Loss of containment most likely to occur where there are weak points in the structures (hopper and import silo) or concrete underground surround (cracks) Weak points could be created through either human damage (during maintenance/operation) or environmental (corrosion) | Both the import silo and hopper is located below ground within the concrete encased containment below ground. The hopper is currently leaking but loss of containment is contained in the concrete encasement and liquid is pumped back to the liquor return. Structural failure of the tank would mainly be through corrosion (bolts, connections between panels) or damage during operation or maintenance. In the case of significant corrosion and leaks forming, the liquid and some cake would seep through the leaks. The volume of cake would however be contained within the underground concrete containment structure and any liquids would drain towards the drainage pump connected to the liquor return. Due to operational presence on site, large drops in levels in the tanks and significant damage (leaks/cracks/corrosion) would be noticed. Total loss of containment of the import silo could occur but would be contained within concrete underground containment. If the concrete encased containment were to fail in conjunction with the hopper/import silo (not deemed to be a credible scenario), the cake liquid could percolate into the permeable soil at a slow rate over a long period. | [6 empty] | > 1 in 1 Million | L
Structural failure - pipework (catastrophic) | Loss of containment due to failure of above ground connecting pipework | In the unlikely event where the above ground pipework (rising mains) or valves fail completely, the volume contained within the pipework could be lost, if the valves are not closed by operational staff. Pumps within the import cake area (drainage and THP silo feed pumps) would also be inhibited immediately by automated safeguards (pressure sensors and indicators on rising main) in place. On site operational staff would promptly respond to any such event. As the site is generally manned, operational staff would be able to manage loss of containment if the pipes were to fail. Any loss of containment from the pipes within the concrete encased containment underground, would be contained and any liquids would drain towards the drainage pump connected to the liquor return. Total loss of containment could occur but unlikely due to type of inventory and would be contained within concrete underground containment. | [6 empty] | > 1 in 1 Million | L
Structural failure - pipework (partial) | Loss of containment most likely to occur where there are weak points in the pipework - Most likely through failures where pipe connects with the structure, bolts/sealant at pipe flanges/valves or along any pipe pitting. Weak point could be created through either human damage (during maintenance/operation), erosion (high velocities and silt content within the pipe) or environmental (corrosion) | All pipework around the import silo is carbon or stainless steel. If partial loss of containment occurs above ground from pipework, due to the impermeable external surfacing around the import silo area, the majority of the cake will most likely stay around the import silo (low viscosity) and any liquid from the cake will cascade into gullies and ultimately liquor return. Due to operational presence on site, significant leaks/damage to pipework would be noticed and loss of containment would be mitigated through operational measures (closing of valves and isolation of tanks/pipework). Operational staff stated that corrosion is a problem on site (due to extremities - site is exposed and close to the ocean). Leaks from corrosion (valves, bolts, pitting in pipework) could therefore cause partial loss of containment. However, significant failure has not occurred. Any loss of containment from the pipes within the concrete encased containment underground, would be contained and any liquids would drain towards the drainage pump connected to the liquor return. Total loss of containment could occur but it is still highly unlikely and would be contained within concrete underground structure. | [6 empty] | < 1 in 100 | H
Vehicular impact (partial to catastrophic) | Impact from vehicles - damage to pipes or tanks causing loss of containment | Vehicular damage assumed mitigated due to existing vehicular impact protection. | [6 empty] | > 1 in 1 Million | L
Vandalism | Vandalism of infrastructure - damage to pipes or tank causing loss of containment | No known vandalism to tanks or pipework - CCTV cameras and automated gates on site as well as 24 hour manned operation. If vandalism damage were to occur, total loss of containment is unlikely due to type of inventory. Partial loss of containment would be more likely to occur if slight damage was done. | [6 empty] | > 1 in 1 Million | L
*Site is manned. Probability and frequency thus reduced
Frequency of loss of containment (Ciria 736) | L
Overall zone hazard rating
Overall zone hazard rating (Ciria 736) | Low
Containment required
Containment required | Class 1
>100m
Ocean/beach
97m
Inlet
Grassy area- potential ecology
50m
Impermeable ground
Permeable ground
Road gullies
04/08/2020
File Ref
Version
B14411-123532-ZZ-XX-AS-ZA-CI1010
P01
Originator
Jacques Calitz
James Croston
Date
Date
30/06/2020
04/08/2020
Checker
Zone 1 (Imported cake silo)
IED CIRIA 736 Risk Assessment
James Croston
Approver
Date
Note on J19: Calitz, Jacques: Add manually. Based on highest risk rating
Note on F63: Calitz, Jacques: Add manually. Based on highest risk rating
Note on J63: Calitz, Jacques: Add manually. Based on highest risk rating
Note on C90: Calitz, Jacques: Add manually. Based on highest risk rating

## Mitigation
Catastrophic failure - modes (loss of containment) - pragmatic solution
Risk | Cause | Existing consequence and mitigation measure | Existing zone risk rating | Proposed Mitigation | Risk rating after mitigation
| Operational failure - tanker (partial - catastrophic) | Filling of silo via 18/25m3 lorries/trucks is done with operational staff present. There has been cake spills within the hopper and silo area (skip overtopping), but that was contained within the secondary concrete containment structure or in the hardstanding area in front of the import cake bays and cleaned. Total loss of containment is unlikely (partial loss of containment would be more likely to occur but would be contained) | L | Reinforced concrete secondary containment is already available for the import silo. The volume of this secondary containment is significantly greater than the cake import silos. 25m3 could be lost above ground from truck/lorry. Spillage can occur through potential skip overtopping. If cake (low viscosity at 22% DS) is spilled on the impermeable hardstanding surface at ground level, this would be in small quantities and can be quickly isolated and cleaned up by trained operational staff manning the site all day, In summary, the zone is robust and safe and no additional mitigation is necessary. | L
| Operational failure - tank (partial) | No known issues with overfilling and overflow. There are level sensors within each of the silos ensuring they are not overfilled. If overfilling occurred, would be contained within the concrete encased containment underground. Total loss of containment is unlikely (partial loss of containment would be more likely to occur but would be contained) | L | In the very unlikely event that import silo/hopper overflows (ultrasonic meter failure), the spillage volume would be low as the site is manned (Assumed volume of one lorry <25m3). There have been no cases of overflow/overfilling reported by the operational team and any overfilling/overflows are mitigated currently by the necessary telemetry controls (cake bays have level monitors showing what level the cake is in each). In the unlikely event of overfilling/overflows any loss of containment within the concrete encased containment underground from the hopper or import silo, would be contained in the secondary containment and any liquids would drain towards the drainage pump connected to the liquor return. Secondary containment is thus not proposed. In summary, the zone is robust and safe and no additional mitigation is necessary. | L
| Structural failure - tank (catastrophic) | Both the import silo and hopper is located below ground within the a concrete secondary containment structure below ground. In the case of significant damage during operation or maintenance, the total volume contained within the import silo and hopper would be contained within the secondary containment concrete structure and any liquids would drain towards the drainage pump connected to the liquor return. Due to operational presence on site, large drops in levels in the tanks and significant damage (leaks/cracks/corrosion) would be noticed. Total loss of containment of the import silo could occur but the inventory would be contained within concrete underground structure. The silos can easily be taken offline to allow any repairs needed to arrest gradual deterioration. If the concrete encased containment were to fail in conjunction with the hopper/import silo (not deemed to be a credible scenario), the cake liquid could percolate into the permeable soil at a slow rate over a long period. | L | If catastrophic failure of the import silo occurs, 40m3 of inventory could potentially be lost. The volume of the secondary containment is significantly greater than the cake import silos. Any liquids derived from the cake would be directed towards the sump in the concrete secondary containment structure and pumped to the liquor return pump station at a controlled rate. The import silo/hopper and the concrete structure shall be structurally inspected as part of the annual sludge plant shutdown for maintenance and condition inspections. If a problem is identified with either containment item such as signs of corrosion in the import silo or spalling or large cracks in the concrete, the tanks can be proactively repaired or refurbished. Ultrasonic meters can signal an alarm if there is a significant and unanticipated drop in level to mitigate any significant loss of containment. The zone is robust and safe and no additional mitigation is considered to be necessary other than ensuring primary and secondary containment condition continues to be observed during weekly maintenance inspections and ensuring structural inspections are undertaken annually by a competent engineer. | L
| Structural failure - tank (partial) | Both the import silo and hopper is located below ground within the concrete encased containment below ground. The hopper is currently leaking but loss of containment is contained in the concrete encasement and liquid is pumped back to the liquor return. Structural failure of the tank would mainly be through corrosion (bolts, connections between panels) or damage during operation or maintenance. In the case of significant corrosion and leaks forming, the liquid and some cake would seep through the leaks. The volume of cake would however be contained within the underground concrete containment structure and any liquids would drain towards the drainage pump connected to the liquor return. Due to operational presence on site, large drops in levels in the tanks and significant damage (leaks/cracks/corrosion) would be noticed. Total loss of containment of the import silo could occur but would be contained within concrete underground containment. If the concrete encased containment were to fail in conjunction with the hopper/import silo (not deemed to be a credible scenario), the cake liquid could percolate into the permeable soil at a slow rate over a long period. | L | If partial failure of the import silo occurs, up to 40m3 of inventory could potentially be lost. The volume of the secondary containment is significantly greater than the cake import silos. Any liquids derived from the cake would be directed towards the sump in the concrete secondary containment structure and pumped to the liquor return pump station at a controlled rate. The import silo/hopper and the concrete structure shall be structurally inspected as part of the annual sludge plant shutdown for maintenance and condition inspections. If a problem is identified with either containment item such as signs of corrosion in the import silo or spalling or large cracks in the concrete, the tanks can be proactively repaired or refurbished. Ultrasonic meters can signal an alarm if there is a significant and unanticipated drop in level to mitigate any significant loss of containment. In summary, the zone is robust and safe and no additional mitigation is considered to be necessary other than ensuring primary and secondary containment condition continues to be observed during weekly maintenance inspections and ensuring structural inspections are undertaken annually by a competent engineer. | L
| Structural failure - pipework (catastrophic) | In the unlikely event where the above ground pipework (rising mains) or valves fail completely, the volume contained within the pipework could be lost, if the valves are not closed by operational staff. Pumps within the import cake area (drainage and THP silo feed pumps) would also be inhibited immediately by automated safeguards (pressure sensors and indicators on rising main) in place. On site operational staff would promptly respond to any such event. As the site is generally manned, operational staff would be able to manage loss of containment if the pipes were to fail. Any loss of containment from the pipes within the concrete encased containment underground, would be contained and any liquids would drain towards the drainage pump connected to the liquor return. Total loss of containment could occur but unlikely due to type of inventory and would be contained within concrete underground containment. | L | Any volume lost within the pipework can be accommodated in the hardstanding area around the tank and pipework within the drainage system, due to the type of inventory. Any liquors from the cake would drain to the local drainage system and then to the liquor return pump station. Operational staff stated that there have been pipe leaks on site due to the extremities (corrosion), however, any significant corrosion is repaired if significant. All pipework and chambers should be inspected structurally for any leaks and falling head tests conducted where appropriate. Any defects should be identified and pipework and chambers refurbished if necessary. In the unlikely event that tank loses containment through pipework above ground, based on topography and the type of inventory, loss of containment would be limited to the hardstanding area around the import silo (cake has a low viscosity). A portion of the liquid from the cake could cascade towards the gullies which is connected to the liquor return PS, but would be minimal. Any loss of containment from the pipes within the concrete encased containment underground, would be contained and any liquids would drain towards the drainage pump connected to the liquor return. In summary, the zone is robust and safe and no additional mitigation is considered to be necessary other than ensuring condition assessments of above ground pipework continues during weekly maintenance inspections with annual inspections of above ground ad below ground pipework and structures by a competent engineer. | L
| Structural failure - pipework (partial) | All pipework around the import silo is carbon or stainless steel. If partial loss of containment occurs above ground from pipework, due to the impermeable external surfacing around the import silo area, the majority of the cake will most likely stay around the import silo (low viscosity) and any liquid from the cake will cascade into gullies and ultimately liquor return. Due to operational presence on site, significant leaks/damage to pipework would be noticed and loss of containment would be mitigated through operational measures (closing of valves and isolation of tanks/pipework). Operational staff stated that corrosion is a problem on site (due to extremities - site is exposed and close to the ocean). Leaks from corrosion (valves, bolts, pitting in pipework) could therefore cause partial loss of containment. However, significant failure has not occurred. Any loss of containment from the pipes within the concrete encased containment underground, would be contained and any liquids would drain towards the drainage pump connected to the liquor return. Total loss of containment could occur but it is still highly unlikely and would be contained within concrete underground structure. | L | Any volume lost within the pipework can be accommodated in the hardstanding area around the tank and pipework within the drainage system, due to the type of inventory. Any liquors from the cake would drain to the local drainage system and then to the liquor return pump station. Operational staff stated that there have been pipe leaks on site due to the extremities (corrosion), however, any significant corrosion is repaired if significant. All pipework and chambers should be inspected structurally for any leaks and falling head tests conducted where appropriate. Any defects should be identified and pipework and chambers refurbished if necessary. In the unlikely event that tank loses containment through pipework above ground, based on topography and the type of inventory, loss of containment would be limited to the hardstanding area around the import silo (cake has a low viscosity). A portion of the liquid from the cake could cascade towards the gullies which is connected to the liquor return PS, but would be minimal. Any loss of containment from the pipes within the concrete encased containment underground, would be contained and any liquids would drain towards the drainage pump connected to the liquor return. In summary, the zone is robust and safe and no additional mitigation is considered to be necessary other than ensuring condition assessments of above ground pipework continues during weekly maintenance inspections with annual inspections of above ground and below ground pipework and structures by a competent engineer. | L
| Vehicular impact (partial to catastrophic) | Vehicular damage assumed mitigated due to existing vehicular impact protection. | L | No mitigation measures proposed, existing measures deemed adequate. The existing measures mitigate any potential impacts from vehicles and potential damage which could lead to loss of containment. | L
| Vandalism | No known vandalism to tanks or pipework - CCTV cameras and automated gates on site as well as 24 hour manned operation. If vandalism damage were to occur, total loss of containment is unlikely due to type of inventory. Partial loss of containment would be more likely to occur if slight damage was done. | L | No mitigation measures proposed, existing measures deemed adequate. If pipes and the tank get damaged, because it is operated on a daily basis with operational staff present, the risk of loss of containment is low. If there are any signs of damage due to vandalism operators will fix any damage first. | L
The probability and risk of failure from the tanks is low and any associated loss of inventory volume would be contained within the secondary containment reinforced concrete structure. As per CIRIA 736, no further measures to improve the containment infrastructure are deemed necessary for the Zone. The site maintenance strategy and annual plant shutdown does need to include annual structural assessments of the containment structures and pipework by a competent engineer to allow for pro-active maintenance.
04/08/2020
File Ref
Version
B14411-123532-ZZ-XX-AS-ZA-CI1010
P01
Originator
Jacques Calitz
James Croston
Date
Date
30/06/2020
04/08/2020
Checker
Zone 1 (Imported cake silo)
IED CIRIA 736 Risk Assessment
James Croston
Approver
Date

## List (hidden)
Possible Combination |  |  |  | Site Hazard Rating | LLL | MLL | HLL
L | L | L | LLL | L | LLM | MLM | HLM
M | M | L | MML | L | LLH | MLH | HLH
M | L | L | MLL | L | LMM | MMM | HMM
H | L | L | HLL | L | LML | MML | HML
M | M | M | MMM | M | LMH | MMH | HMH
H | M | L | HML | M | LHL | MHL | HHL
H | H | L | HHL | M | LHM | MHM | HHM
H | M | M | HMM | H | LHH | MHH | HHH
H | H | M | HHM | H
H | H | H | HHH | H
< 1 in 100 |  |  | H
1 in 100 to 1 in 1 Million |  |  | M
> 1 in 1 Million |  |  | L
H | H | HH | High
H | M | HM | High
M | H | MH | High
M | M | MM | Moderate
H | L | HL | Moderate
L | H | LH | Moderate
L | L | LL | Low
M | L | ML | Low
L | M | LM | Low
Low |  | Class 1
Moderate |  | Class 2
High |  | Class 3