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Notice of variation and consolidation 

Notice of variation and consolidation with introductory note
The Environmental Permitting (England & Wales) Regulations 2016

Bourne Leisure Limited 

Wastewater Treatment Works and Combined Storm Overflow serving 

Hafan Y Mor Holiday Park 
Chwilog 
Pwllheli 
Gwynedd 
LL53 6HX 


Variation application number
PAN-033874
Permit number
CG0151702




Wastewater Treatment Works and Combined 
Storm Overflow serving  
Hafan Y Mor Holiday Park
Permit number CG0151702
Introductory note
This introductory note does not form a part of the notice.

The following notice gives notice of the variation and consolidation of an environmental permit.

Operator initiated variation to amend National Grid Refences in Table S3.4 and site plan.

The schedules specify the changes made to the permit.

The status log of a permit sets out the permitting history, including any changes to the permit reference number.  It is not backdated before 6 April 2010. 

	Status log of the permit

	Description
	Date
	Comments

	Application PAN-002054
(variation and consolidation)
	Duly made 17/10/2017
	Application to vary and update the permit to modern conditions and amend operator name.

	Variation determined CG0151702
	16/02/2018
	Varied and consolidated permit issued in modern condition format.

	Application PAN-033874
(variation and consolidation)
	Duly made
03/09/2026
	Application updating monitoring point National Grid Refences in Table S3.4 and site plan

	Variation determined CG0151702 
	12/11/2026
	Varied and consolidated permit issued in modern condition format.





End of introductory note
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Notice of variation and consolidation 


The Environmental Permitting (England and Wales) Regulations 2016

[bookmark: _Hlt13295849][bookmark: OperatorName2]The Natural Resources Body for Wales (“Natural Resources Wales”) in exercise of its powers under regulation 20 of the Environmental Permitting (England and Wales) Regulations 2016 varies and consolidates

permit number
CG0151702

issued to:
Bourne Leisure Limited  (“the operator”),
whose registered office is

No1 Park Lane 
Hemel Hempstead
Hertfordshire 
HP2 4YL 
company registration number 04011660

to operate a regulated facility at

Hafan Y Mor Holiday Park 
Chwilog 
Pwllheli 
Gwynedd  
LL53 6HX 

to the extent set out in the schedules.

The notice shall take effect from 12/11/2026

	Name
	Date

	Katrin Raynor
	12/11/2026



Authorised on behalf of Natural Resources Wales

Schedule 1 
The following conditions were varied as a result of an Natural Resources Wales initiated variation:
· 2.3 Operating Technique
· 3.1.2 Emissions To Water
The following conditions were varied as a result of the application made by the operator:
· Table S3.4
· Schedule 7 Site plans


Schedule 2 – consolidated permit
Consolidated permit issued as a separate document. 
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Permit


The Environmental Permitting (England and Wales) Regulations 2016

Permit number 
CG0151702
This is the consolidated permit referred to in the variation and consolidation notice for application insert application number authorising, 

Bourne Leisure Limited  (“the operator”),
whose registered office is

No1 Park Lane 
Hemel Hempstead
Hertfordshire 
HP2 4YL 

company registration number 04011660
to operate a water discharge activity at

Hafan Y Mor Holiday Park 
Chwilog 
Pwllheli 
Gwynedd  
LL53 6HX 
to the extent authorised by and subject to the conditions of this permit.

The permit variation and consolidation shall take effect from 12/11/2026

	Name
	Date

	Katrin Raynor
	12/11/2026


Authorised on behalf of Natural Resources Wales


  
Conditions
Management
0. [bookmark: _Ref373938749]General management
[bookmark: _Ref373938830]The operator shall manage and operate the activities:
in accordance with a written management system that identifies and minimises risks of pollution so far as is reasonably practicable, including those risks arising from operations, maintenance, accidents, incidents, non-conformances and those drawn to the attention of the operator as a result of complaints; and
using sufficient competent persons and resources.
Records demonstrating compliance with condition 1.1.1 shall be maintained. 
Any person having duties that are or may be affected by the matters set out in this permit shall have convenient access to a copy of the permit.
Operations
Permitted activities
The only activities authorised by the permit are the activities specified in schedule 1 table S1.1.
The site 
The discharge activities shall take place at the discharge points marked on the site plans at schedule 7 to this permit, and as listed in table S3.2.
Operating techniques
2.3. 	For the discharge(s) specified in table S3.3:
The discharge shall only occur when and only for as long as the flow passed forward is equal to or greater than the overflow setting indicated due to rainfall and/or snow melt.
On-line storm storage must be fully utilised before a discharge occurs. It shall only fill with the excess flows due to rainfall and/or snow melt. The storage shall be emptied and its contents returned to the continuation flow as soon as reasonably practicable. The minimum on-line storm storage required is specified in table S3.3. 
The discharge shall not be comminuted or macerated and shall have passed through screens as specified and shall not contain a significant quantity of solid matter with a particle size greater than any indicated. All screenings shall be removed from the discharge.
Where a mechanically cleaned screen is installed, a telemetry alarm system shall be installed and maintained so as to give the operator immediate notification of a failure of the screen cleaning mechanism, unless otherwise agreed in writing by Natural Resources Wales. The operator shall take all appropriate measures to return the screen cleaning mechanism to normal operation as soon as reasonably practicable after receipt of notification of the failure.



Emissions and monitoring
Emissions to water
The limits given in schedule 3 table S3.1 shall not be exceeded.
0.0.1 The permitted Dry Weather Flow limit in schedule 3 table S3.1 is set at the operator`s planned annual 80% exceeded daily volume discharged. 
(a) For compliance purposes an exceedance shall be recorded for a calendar year only when the limit in effect on 31 December of that calendar year is exceeded by 90% or more of the ‘good’ recorded Total Daily Volumes in that calendar year. 
(b) Until 1 January 2027
(i) If an exceedance of the Dry Weather Flow limit is recorded in a calendar year then the operator shall, as soon as is practicable, investigate the reasons for the exceedance. 
(ii) The operator shall report the reasons for the exceedance to Natural Resources Wales and the steps that it proposes to take to restore compliance. 
(iii) An exceedance of the Dry Weather Flow limit shall not be recorded as a failure of the Dry Weather Flow limit in that calendar year if the operator takes appropriate steps to restore compliance. 
(c)       From 1 January 2027 The limit has been complied with in an assessment calendar year unless; 
(iv) the limit was exceeded in the compliance assessment calendar year and, 
(v) two or more exceedances have occurred in the preceding 4 calendar years. 
Only exceedances from a calendar year after 31 December 2026 shall be used. 
Emissions of substances not controlled by emission limits
For the activity A1 referenced in schedule 1, table S1.1 The operator shall take appropriate measures to minimise so far as reasonably practicable the polluting effects of the emissions of substances in the discharge not controlled by emission limits (excluding odour).
Monitoring 
The operator shall, unless otherwise agreed in writing by Natural Resources Wales, undertake the monitoring specified in the following tables in schedule 3 to this permit:
point source emissions specified in tables S3.1 and S3.4;
inlet quality specified in tables S3.1 and S3.4.
The operator shall maintain records of all monitoring required by this permit.
Monitoring equipment, techniques, personnel and organisations employed for the emissions monitoring programme [and the environmental or other monitoring] specified in condition 3.3.1 shall have either MCERTS certification or MCERTS accreditation (as appropriate), where available, unless otherwise agreed in writing by Natural Resources Wales.
Accessible monitoring points shall be provided and maintained to enable the emissions monitoring programme to be carried out at the monitoring points specified in table [S3.4] of schedule 3 and shown marked on the site plans in schedule 7. 
	Effective from the date of installation of EDM monitoring equipment at the Site: The Operator shall take appropriate measures to ensure that the event recorder remains fully operational at all times within the reference period specified in table S3.1. Any failures shall be remedied as soon as reasonably practicable.


Information
Records
All records required to be made by schedule 3, 4 and 5 to this permit shall:
be legible;
be made as soon as reasonably practicable;
if amended, be amended in such a way that the original and any subsequent amendments remain legible, or are capable of retrieval; and
be retained, unless otherwise agreed in writing by Natural Resources Wales, for at least 6 years from the date when the records were made. 
The operator shall maintain convenient access, in either electronic or hard copy, to the records, plan and management system required to be maintained by this permit. 
Reporting
The operator shall send all reports and notifications required by the permit to Natural Resources Wales using the contact details supplied in writing by Natural Resources Wales.
Within the time period after the end of the reporting period specified in schedule 4 table S4.1 the operator shall, unless otherwise agreed in writing by Natural Resources Wales, submit reports of the monitoring and assessment carried out in accordance with the conditions of this permit, as follows:
in respect of the parameters and monitoring points specified in schedule 4 table S4.1;
[for the reporting periods specified in schedule 4 table S4.1 and] using the forms specified in schedule 4 table S4.2; and
giving the information from such results and assessments as may be required by the forms specified in those tables.
On request, the Operator shall supply Natural Resources Wales with written details of individual spill event(s).
Notifications
Natural Resources Wales shall be notified as soon as reasonably practicable following detection, within the site of the regulated facility of:
(a) any malfunction, breakdown or failure of equipment or techniques, accident, or emission of a substance not controlled by an emission limit which has caused, is causing or may cause significant pollution; and
any breach of a limit specified in schedule 3 table S3.1 (including individual exceedances of limits which are covered by condition 3.1.2).
Any other significant adverse environmental effects, which may have been caused by the activity, shall also be notified to Natural Resources Wales as soon as reasonably practicable following detection.
The information provided under condition 4.3.1 shall be supported by sending the information listed in schedule 5 to this permit within the time period specified in that schedule.
Natural Resources Wales shall be notified within 14 days of the occurrence of the following matters, except where such disclosure is prohibited by Stock Exchange rules:
Where the operator is a registered company:
any change in the operator’s trading name, registered name or registered office address; and
any steps taken with a view to the operator going into administration, entering into a company voluntary arrangement or being wound up.
Where the operator is a corporate body other than a registered company:
(c) any change in the operator’s name or address; and
any steps taken with a view to the dissolution of the operator.
For the activity A1 referenced in schedule 1, table S1.1 where the operator proposes to make a change in the nature of the activity by increasing the concentration of, or the addition of, or allowing the introduction of, a substance to the activity to an extent that the operator considers could have a significant adverse environmental effect on the receiving waters, and the change is not permitted by emission limits specified within schedule 3 table S3.1 or the subject of an application for approval under the EP Regulations or under the terms of this permit:
Natural Resources Wales shall be notified in writing at least 14 days before the increase or addition or allowing the introduction; and
the notification shall contain a description of the proposed change.
Interpretation
In this permit the expressions listed in schedule 6 shall have the meaning given in that schedule.
In this permit references to reports and notifications mean written reports and notifications, except where reference is made to notification being made “as soon as reasonably practicable”, in which case it may be provided by telephone.

Schedule 1 – Operations 

	Table S1.1 Activities

	Activity reference
	Description of activity
	Limits of specified activity

	A1
	Discharge of secondary treated sewage effluent via Outlet 1
	N/A

	A2
	Discharge of settled storm sewage via Outlet 1
	All available storm storage and pumping capacity to the WwTW must be fully utilised before a spill can occur


 
	Table S1.2 Operating techniques

	Table S1.2 not in use






Schedule 2 – Waste types, raw materials and fuels
Schedule 2 not in use.



Schedule 3 – Emissions and monitoring

	Table S3.1 Point Source emissions to water (other than sewer) – emission limits and monitoring requirements

	Effluent(s) and discharge point(s)
	Parameter  
	Limit (including unit)
	Reference Period
	Limit of effective range
	Monitoring frequency
	Compliance Statistic

	A1 Secondary treated sewage effluent via Outlet 1
	Dry weather flow
	780 m3/day


	Total daily volume
	N/A                                                                
	Continuous
	Conditions 3.1.2 applies

	
	15-minute instantaneous or averaged flow
	No limit set. Record as l/s
	15 minute
	N/A
	Continuous
	N/A

	
	ATU-BOD as O2
	40 mg/l
	Instantaneous (spot sample)
	N/A
	N/A
	Maximum

	
	Suspended solids (measured after drying at 105oC)

	60 mg/l
	Instantaneous (spot sample)
	N/A
	N/A
	Maximum

	
	Visible oil or grease
	No significant trace present so far as is reasonably practicable
	Instantaneous (visual examination )
	N/A
	N/A
	No significant trace


	A2 Storm sewage via Outlet 1


	Discharge start and end times

	N/A


	N/A


	N/A


	Whenever a discharge occurs
	N/A



	
	Block  counted  spills
	N/A
	1st January to 31st December inclusive
	N/A
	15 minutes
	N/A

	
	Event recorder status operational 
	N/A
	N/A
	N/A
	15 minutes
	N/A



	Table S3.2 Discharge points

	Effluent Name
	Discharge Point
	 Discharge point NGR
	Receiving water/Environment

	A1 Secondary treated sewage effluent 
	Outlet 1

	SH 44404 35985

	Tremadoc Bay


	A2 Settled storm sewage
	
	
	



	Table S3.3 Storm sewage discharge settings

	Effluent(s) and discharge point(s) 
	Description of discharge
	Overflow setting l/s
	Maximum size of solid matter
	Screen aperture
size
	Minimum screen capacity flow l/s
	Minimum  storage capacity m3 (on-line)

	A2 Settled storm sewage via Outlet 2
	Settled storm sewage
	45
	No greater than 6 mm in more than 1 dimension

	6 mm x 6 mm 


	All flows shall be screened, 
	162



	Table S3.4 Monitoring points

	Effluent(s) and discharge point(s)
	Monitoring type
	Monitoring point NGR
	Monitoring point reference

	A1 Secondary treated sewage effluent via Outlet 1 
	Flow monitoring point
	SH 43767 37070
	Flow and final effluent sample monitoring point

	
	Inlet sampling point 
	SH 43735 37068
	Inlet sample point

	
	Final effluent sampling point
	SH 43767 37070
	Flow and final effluent sample monitoring point

	A2 Settled storm sewage via Outlet 2
	Storm Effluent sampling
	SH 43718 36737
	CSO sample point

	
	Event duration monitoring
	SH 43718 36737
	




Schedule 4 – Reporting
Parameters, for which reports shall be made, in accordance with conditions of this permit, are listed below.
	Table S4.1 Reporting of monitoring data

	Parameter
	Monitoring point reference
	Reporting period
	Period begins

	Dry Weather Flow (daily flows total)
	Flow monitoring point
	Annually
Report to be submitted within 2 months of the end of the calendar year
	1 January

	15-minute flow
	Flow monitoring point
	Reports to be provided to Natural Resources Wales upon request 
Report to be submitted within 28 days unless otherwise specified in writing by Natural Resources Wales
	Upon request by Natural Resources Wales

	CSO performance, including adjusted number of total spills

	CSO sample point
	Annually
Report to be submitted within 2 months
	1 January

	Duration of total spills

	CSO sample point
	Annually
Report to be submitted within 2 months
	1 January

	Event recorder status operational

	CSO sample point
	Annually
Report to be submitted within 2 months
	1 January

	Storm sewage discharge start and end times

	CSO sample point
	Reports to be provided to Natural Resources Wales upon request 
	As specified by Natural Resources Wales



	Table S4.2 Reporting forms

	Parameter
	Reporting format

	Dry Weather Flow (daily flows total)
	Form as agreed in writing by Natural Resources Wales

	15-minute flow
	Form as agreed in writing by Natural Resources Wales Wales

	Combined sewer overflow performance including number and duration of block counted spills
	Annual  form as agreed in writing by Natural Resources Wales

	Storm sewage discharge start and end times
	Form as agreed in writing by Natural Resources Wales 

	Event recorder status
	Form as agreed in writing by Natural Resources Wales 
Percentage of time in the recording period that event duration monitoring equipment is operational

	Investigation into the operation of the overflow
	Electronic format as agreed in writing by Natural Resources Wales. 


[image: ]
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Schedule 5 – Notification 
These pages outline the information that the operator must provide. 
Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.
If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.
Part A
	Permit Number
	CG0151702

	Name of operator
	

	Location of Facility
	Hafan Y Mor Holiday Park

	Time and date of the detection 
	



	(a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques,  accident, or emission of a substance not controlled by an emission limit which has caused, is causing or may cause significant pollution

	To be notified within 24 hours of detection unless otherwise agreed in writing by the Natural Resources Wales.

	Date and time of the event
	

	Reference or description of the location of the event 
	

	Description of where any release into the environment took place
	

	Substances(s) potentially released/type or nature of sewage released
	

	Best estimate of the quantity or rate of release of substances and/or duration of discharge
	

	Best estimate of the environmental impact of the discharge
	

	Measures taken, or intended to be taken, to stop any emission
	

	Description of the failure or accident.
	



	(b) Notification requirements for the breach of a limit specified in schedule 3 table S3.1

	The information specified below is to be notified to Natural Resources Wales as soon as reasonably practicable following detection.

	Monitoring point reference/ source
	

	Self monitoring regime (where relevant)
	e.g. OSM/UWWTR


	Type of failure 
	e.g. Flow monitoring / CSO operation


	Date of sample/event
	

	Parameter
	

	Result and units
	

	Limit and units
	



Part B – to be submitted as soon as reasonably practicable unless otherwise agreed in writing by Natural Resources Wales
	Any more accurate information on the matters for notification under Part A.
	

	Measures taken, or intended to be taken, to prevent a recurrence of the incident/breach/exceedance
	

	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission
	



	Name*
	

	Post
	

	Signature
	

	Date
	


* authorised to sign on behalf of the operator


Schedule 6 – Interpretation 
“abnormal operating conditions” include but are not limited to, the circumstances described in Regulation 40(1) of, or paragraph 6(5) of Schedule 21 to, the Environmental Permitting Regulations 2016 (illegal discharge to sewer), unusual weather, or during a defined period where the permit authorising the permitted activity has been varied for reasons such as capital works construction.
“accident” means an accident that may result in pollution.
"annually" means once every year.
“application” means the application for this permit, together with any additional information supplied by the operator as part of the application and any response to a notice served under Schedule 5 to the EP Regulations.
For the activity A1 referenced in schedule 1, table S1.1 “appropriate measures” for the purposes of the emission of substances not controlled by emission limits condition (condition 3.2.1) do not require the operator to undertake treatment to a level beyond that specified in schedule 1 table S1.1, or to carry out routine monitoring for substances not controlled by emission limits.
“ATU-BOD as O2” means the biochemical oxygen demand (measured after 5 days at 20oC with nitrification suppressed by the addition of allylthiourea).
“block counted spill” one or more overflow events within a period of 12 hours or less will be considered to be one spill, one or more overflow events extending over a period of greater than 12 hours up to 36 hours will be considered to be 2 spills. Each subsequent 24 hour duration counts as 1 additional spill and the whole of the 24 hour block is included. 
“COD as O2” means the chemical oxygen demand (measured using the standard dichromate procedure).
“emissions of substances not controlled by emission limits” means emissions of substances to air, water or land from the permitted activities, which are not controlled by an emission limit.
“EP Regulations” means The Environmental Permitting (England and Wales) Regulations SI 2016 No.1154 and words and expressions used in this permit which are also used in the Regulations have the same meanings as in those Regulations.
"event recorder" a recorder which records the start time and  end time of individual overflow events.
“Formula A” is defined as (PG+I+E) + 1360P + 2E litres/day.  Where P = population served, G = water consumption per head per day (litres/head/day) I = infiltration (litres/day) E = trade effluent flow to sewer (litres/day)
“MCERTS” means the Environment Agency’s Monitoring Certification Scheme.
“minimum screen capacity flow” means the minimum flow passed through the screens to the outfall when the screen bypass operates. 
“monitoring frequency” as used in Table S3.1 in the context of event duration monitoring is the temporal interval at which a change in state between no discharge and discharge is to be detected.
“Natural Resources Wales” means the Natural Resources Body for Wales established by article 3 of the Natural Resources Body for Wales (Establishment) Order 2012. The Natural Resources Body for Wales (Functions) Order 2013 transferred the relevant functions of the Countryside Council for Wales, and functions of the Environment Agency and the Forestry Commission in Wales to the Natural Resources Body for Wales.
“overflow” for the purposes of schedule 7, overflow means the weir or orifice or other control which directs excess flow away from the continuation sewer when the flow exceeds the overflow setting due to rainfall and/or snowmelt.
“overflow event” any individual operation, of any duration, of the event recorder or any recorded discharge of sewage from the outfall.
“overflow setting” means the minimum flow passed forward to the continuation sewer when the overflow operates.
"quarter" means a calendar year quarter commencing on 1 January, 1 April, 1 July or 1 October.
“significant pollution” means a high level impact incident as indicated by NRW incident classification system.
[bookmark: OLE_LINK1][bookmark: OLE_LINK2]“significant spill” any spill that has not been demonstrated to have been, or measured as being, less than 50 m3 in volume.
“unusual weather conditions” includes, but is not limited to:
low ambient temperatures, or the freezing of mechanical equipment in the works;
significant snow deposits;
tidal or fluvial flooding;
weather conditions causing unforeseen loss of power supply to the sewage treatment that could not be ameliorated by the reasonable provision and operation of standby generation facilities.
“Urban Waste Water Treatment (England and Wales) Regulations 1994 (UWWTR)” means Urban Waste Water Treatment (England and Wales) Regulations 1994 SI 2841and the words and expressions used in this permit which are also used in the Regulations have the same meanings as in those Regulations.
“year” means calendar year ending 31 December.


Schedule 7 – Site plan(s)[image: ] [image: ]
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© Crown Copyright and database right 2026. Ordnance Survey licence number 100019741.
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