| Permit Number: | PAN-003574 | Operator: | PeakGen Power 6 Limited |
| --- | --- | --- | --- |
| Facility: | PeakGen Power Limited, Penarth | Form Number: | Air1 / 13/06/19 |

Reporting of emissions to air for the period from 13/06/2019 to 13/06/2022

| Emission Point | Substance / Parameter | Emission Limit Value | Reference Period | Result [1] | Test Method [2] | Sample Date and Times [3] | Uncertainty [4] |
| --- | --- | --- | --- | --- | --- | --- | --- |
| G1 | Oxides of nitrogen (NO and NO2 expressed as NO2) | 190 mg/m3 | Periodic (average over one hour) | 146.8 mg/m3 | MCERTS BS EN 14792 | 30/10/2019 11:58 -30/10/2019 12:58 | 6.9% |
| G2 |  |  |  | 120.0 mg/m3 |  | 30/10/2019 13:35 -30/10/2019 14:35 | 5.7% |
| G3 |  |  |  | 148.5 mg/m3 |  | 30/10/2019 10:33 -30/10/2019 11:33 | 7.0% |
| G4 |  |  |  | 113.9 mg/m3 |  | 30/10/2019 14:50 -30/10/2019 15:50 | 5.4% |
| G5 |  |  |  | 149.7 mg/m3 |  | 29/10/2019 14:21 -29/10/2019 15:21 | 7.0% |
| G6 |  |  |  | 140.9 mg/m3 |  | 30/10/2019 16:13 -30/10/2019 17:13 | 6.6% |
| G7 |  |  |  | 142.9 mg/m3 |  | 29/10/2019 13:01 -29/10/2019 14:01 | 6.7% |
| G8 |  |  |  | 149.8 mg/m3 |  | 31/10/2019 08:24 -31/10/2019 09:24 | 8.3% |
| G9 |  |  |  | 145.2 mg/m3 |  | 29/10/2019 11:35 -29/10/2019 12:35 | 6.8% |
| G10 |  |  |  | 150.2 mg/m3 |  | 31/10/2019 09:40 -31/10/2019 10:40 | 8.4% |

- The result given is the maximum value (or the minimum value in the case of a limit that is expressed as a minimum) obtained during the reporting period, expressed in the same terms as the emission limit value. Where the emission limit value is expressed as a range, the result is given as the ‘minimum – maximum’ measured values.

- Where an internationally recognised standard test method is used the reference number is given. Where another method that has been formally agreed with Natural Resources Wales is used, then the appropriate identifier is given. In other cases the principal technique is stated, for example gas chromatography.

- For non-continuous measurements the date and time of the sample that produced the result is given. For continuous measurements the percentage of the process operating time covered by the result is given.

- The uncertainty associated with the quoted result at the 95% confidence interval, unless otherwise stated.

Signed ………………………………………….  		Date……02/12/2019.

(Authorised to sign as representative of Operator)