This form covers all DCWW operations environmental pollution and MCerts Flow meter issues.

The Originator must mark either box A or B and then Email the form as detailed below for onward transmission to the EA / NRW.

| Unplanned Event |  |  | X |  | Planned Event |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| To the Smart Hub Risk team at Linea for onward transmission to EA / Natural Resources Wales |  |  |  |  |  |  |  |  |  |  |  |  |  |
| E-mail: | smarthub@dwrcymru.com |  |  |  |  | Telephone: |  |  |  | 0303 313 0103 |  |  |  |
| To Be Completed By DCWW: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Name: |  | John Benson |  |  |  | Job Role: |  |  |  |  |  |  |  |
| Date: |  | 20/12/2019 |  |  |  | Time: |  |  |  | 08:58 |  |  |  |
| Office: |  |  |  |  |  | Phone: |  |  |  |  |  |  |  |
| Fax: |  |  |  |  |  | E mail: |  |  |  |  |  |  |  |
| Details Of Notification: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Asset Type (WwTW, Pstn, CSO, EO, service reservoir, trunk sewer, WTW, storm treatment etc) |  | SPS |  |  |  |  | Permit No: |  |  |  |  |  |  |
| Location: |  | Underwood - Track Next to 14 Larch Grove Llanmartins Newport NP18 2EW |  |  |  |  | Grid Ref: |  |  |  | ST3795988802 |  |  |
|  |  |  |  |  |  |  | Watercourse: |  |  |  |  |  |  |
| Date of Occurrence: |  | 20/12/2019 08:58:17 |  |  |  |  | Expected Duration: |  |  |  | 20/12/2019 14:58:17 |  |  |
| M Cert Related: |  | Y/N |  |  |  |  | Photographic Evidence |  |  |  | Y/N |  |  |
| Brief Outline: |  | Burst on rising main at Wilcrick SPS, valve needs replacing at SPS. Isolating Underwood SPS to ensure a safe repair can be carried out. |  |  |  |  |  |  |  |  |  |  |  |
| Remedial Action: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Actions Taken to Reduce Future Risks: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Environmental Impact: |  | No environmental impact expected - flows to pass through storm screen to reen as per storm consent. Pumping from Underwood SPS is automatically inhibited during storm conditions, but has been manually isolated to prevent the inhibit automatically being removed should storm conditions cease (unlikely due to current heavy rainfall). |  |  |  |  |  |  |  |  |  |  |  |
| Updates: |  | Further updates to follow |  |  |  |  |  |  |  |  |  |  |  |
| DCWW Ref: |  | 315346167 |  | Message No: |  |  |  |  | Update / Final: |  |  | Initial |  |
| Smart Hub Analyst: |  | David Thomson |  | Date: |  |  |  | 20/12/2019 | Time: |  |  | 09:04 |  |