## TNP Verification Report SO2
Transitional National Plan Annual Verification Report (V1.0) |  |  |  | TNP YEAR |  | 4 (2019)
TNP Species: NOx or SO2 or Dust | SO2 | ELV1: (mg/m3) | 440 | LCP: (TNP ref.) |  | 283
Process Operator: RWE Generation UK plc |  |  | Permit No: |  | RP3133LD
Address: Aberthaw Power Station, The Leys, Aberthaw, Near Barry, Vale of Glamorgan, CF62 4ZW |  |  | TNP Contact: |  | Neil Lebbern
|  |  | Tel No: |  | 07584703227
|  |  | Email: |  | neil.lebbern@rwe.com
EN 15259 (Representative Sampling)
EN 15259: (PASS/FAIL) | PASS |  | Test Date(s): |  | 2nd June 2010
Non-Compliances: (including stratification factors if applied in addition to QAL2 factors)
QAL1 (Instrument Suitability)
Make/Model: Pulsi 200 Series |  |  |  |  | MCERTS: Yes (Y/N) |  | MC990006/07
Manufacturer: Procal |  |  |  |  | Sample Type2: | In-Situ IR
QAL2 (Calibration)3 Low Range
LCP unit within windshield or Instrument number: | - | Unit 7 | Unit 8 | Unit 9
QAL2 Factors: b (gradient)4 | - | 1.0179 | 0.96 | 0.9965
a (offset) | mg/m3 | -1.96 | -1.61 | 3.9
Test date | - | 2019-01-24 | 2016-10-26 | 2019-01-21
Date applied5 | - | 2019-08-22 | 2017-02-01 | 2019-08-28
Variability6 | mg/m3 | 8.2946 | 7.64 | 2.7486
VCR from test data7a | mg/m3 | 149 | 239 | 153
VCR extended (if applicable)7b | mg/m3 | 880 | 639 | 880
Second QAL2 (Calibration) High Range
QAL2 Factors: b (gradient)4 | - | 0.9859 | 1.01 | 0.9985
a (offset) | mg/m3 | -0.9 | -1.69 | 3.54
Test date | - | 2019-01-24 | 2016-10-26 | 2019-01-21
Date applied5 | - | 2019-08-22 | 2017-02-01 | 2019-08-28
Variability6 | mg/m3 | 8.2105 | 7.45 | 2.8604
VCR from test data7a | mg/m3 | 145 | 240 | 153
VCR extended (if applicable)7b | mg/m3 | 880 | 642 | 880
AST (Annual Surveillance Test) High Range
LCP units within windshield: | - | Unit 7 | Unit 8 | Unit 9
Test date | - |  | 2019-02-12
Variability6 | mg/m3 |  | 4.57
Validity (Mean Deviation)6 | mg/m3 |  | 62.83
VCR extended (if applicable)7c | mg/m3 |  | n/a
QAL3 (Ongoing Drift Checks)
Frequency8: | Every | Daily Zero | Daily Zero | Daily Zero | Weekly Span | Weekly Span | Weekly Span
Alarm (Action) Limit: | ppm | 11.5 | 11.5 | 11.5 | 11.5 | 11.5 | 11.5
Warning Limit: | ppm | 7.7 | 7.7 | 7.7 | 7.7 | 7.7 | 7.7
Signature: Neil Lebbern | [5 empty] | Date: 09/01/2020

## TNP Verification Report NOx
Transitional National Plan Annual Verification Report (V1.0) |  |  |  | TNP YEAR |  | 4 (2019)
TNP Species: NOx or SO2 or Dust | NOx | ELV1: (mg/m3) | 605 | LCP: (TNP ref.) |  | 283
Process Operator: RWE Generation UK plc |  |  | Permit No: |  | RP3133LD
Address: Aberthaw Power Station, The Leys, Aberthaw, Near Barry, Vale of Glamorgan, CF62 4ZW |  |  | TNP Contact: |  | Neil Lebbern
|  |  | Tel No: |  | 07584703227
|  |  | Email: |  | neil.lebbern@rwe.com
EN 15259 (Representative Sampling)
EN 15259: (PASS/FAIL) | PASS |  | Test Date(s): |  | 2nd June 2010
Non-Compliances: (including stratification factors if applied in addition to QAL2 factors)
QAL1 (Instrument Suitability)
Make/Model: Pulsi 200 Series |  |  |  |  | MCERTS: Yes (Y/N) |  | MC990006/07
Manufacturer: Procal |  |  |  |  | Sample Type2: | In-Situ IR
QAL2 (Calibration)3 Low Range
LCP unit within windshield or Instrument number: | - | Unit 7 | Unit 8 | Unit 9
QAL2 Factors: b (gradient)4 | - | 0.9908 |  | 0.9466
a (offset) | mg/m3 | -15.4 |  | 2.19
Test date | - | 2019-01-24 |  | 2019-01-21
Date applied5 | - | 2019-08-22 |  | 2019-08-28
Variability6 | mg/m3 | 8.1353 |  | 7.3198
VCR from test data7a | mg/m3 | 687 |  | 581
VCR extended (if applicable)7b | mg/m3 | 1210 |  | 1210
Second QAL2 (Calibration) High Range
QAL2 Factors: b (gradient)4 | - | 1.0274 | 0.94 | 0.9914
a (offset) | mg/m3 | -1.98 | 2.835 | 3.53
Test date | - | 2019-01-24 | 2016-10-26 | 2019-01-21
Date applied5 | - | 2019-08-22 | 2017-02-01 | 2019-08-28
Variability6 | mg/m3 | 7.7399 | 5.97 | 8.2586
VCR from test data7a | mg/m3 | 685 | 869 | 582
VCR extended (if applicable)7b | mg/m3 | 1210 | 1869 | 1210
AST (Annual Surveillance Test) High Range
LCP units within windshield: | - | Unit 7 | Unit 8 | Unit 9
Test date | - |  | 2019-02-12
Variability6 | mg/m3 |  | 3.11
Validity (Mean Deviation)6 | mg/m3 |  | 86.39
VCR extended (if applicable)7c | mg/m3 |  | n/a
QAL3 (Ongoing Drift Checks)
Frequency8: | Every | Daily Zero | Daily Zero | Daily Zero | Weekly Span | Weekly Span | Weekly Span
Alarm (Action) Limit: | ppm | 21.1 | 21.1 | 21.1 | 21.1 | 21.1 | 21.1
Warning Limit: | ppm | 14.1 | 14.1 | 14.1 | 14.1 | 14.1 | 14.1
Signature: Neil Lebbern | [5 empty] | Date: 09/01/2020

## TNP Verification Report Dust
Transitional National Plan Annual Verification Report (V1.0) |  |  |  | TNP YEAR |  | 4 (2019)
TNP Species: NOx or SO2 or Dust | Dust | ELV1: (mg/m3) | 35 | LCP: (TNP ref.) |  | 283
Process Operator: RWE Generation UK plc |  |  | Permit No: |  | EPR/RP3133LD
Address: Aberthaw Power Station, The Leys, Aberthaw, Near Barry, Vale of Glamorgan, CF62 4ZW |  |  | TNP Contact: |  | Neil Lebbern
|  |  | Tel No: |  | 07584703227
|  |  | Email: |  | neil.lebbern@rwe.com
EN 15259 (Representative Sampling)
EN 15259: (PASS/FAIL) | PASS |  | Test Date(s): |  | 2nd June 2010
Non-Compliances: (including stratification factors if applied in addition to QAL2 factors)
QAL1 (Instrument Suitability)
Make/Model: OMD41 |  |  |  |  | MCERTS: Yes (Y/N) |  | MC040042/01
Manufacturer: Erwin Sick (Dust Hunter) |  |  |  |  | Sample Type2: | Cross Duct forward scatter
QAL2 (Calibration)3 Low Range
LCP unit within windshield or Instrument number: | - | Unit 7 | Unit 8 | Unit 9
QAL2 Factors: b (gradient)4 | - | 0.4579 |  | 0.483
a (offset) | mg/m3 | -1.31 |  | 1.42
Test date | - | 2019-01-24 |  | 2019-01-21
Date applied5 | - | 2019-08-22 |  | 2019-08-28
Variability6 | mg/m3 | 2.3398 |  | 2.9888
VCR from test data7a | mg/m3 | 45 |  | 65
VCR extended (if applicable)7b | mg/m3 | n/a |  | n/a
Second QAL2 (Calibration) High Range
QAL2 Factors: b (gradient)4 | - | 2.6164 | 1.208 | 2.4448
a (offset) | mg/m3 | -1.47 | -0.303 | 1.12
Test date | - | 2019-01-24 | 2013-03-01 | 2019-01-21
Date applied5 | - | 2019-08-22 | 2014-02-14 | 2019-08-28
Variability6 | mg/m3 | 2.7367 | 0.83 | 2.7434
VCR from test data7a | mg/m3 | 42 | 25.8 | 47
VCR extended (if applicable)7b | mg/m3 | n/a | 55 | n/a
AST (Annual Surveillance Test) High Range
LCP units within windshield: | - | Unit 7 | Unit 8 | Unit 9 | Unit 7 | Unit 8 | Unit 9
Test date | - |  | 2019-02-12
Variability6 | mg/m3 |  | 8.28
Validity (Mean Deviation)6 | mg/m3 |  | 7.5
VCR extended (if applicable)7c | mg/m3 |  | n/a
QAL3 (Ongoing Drift Checks)
Frequency8: | Every | Daily Zero | Daily Zero | Daily Zero | Weekly Span | Weekly Span | Weekly Span
Alarm (Action) Limit: | % | 1.4 | 1.4 | 1.4 | 1.4 | 1.4 | 1.4
Warning Limit: | % | 1.1 | 1.1 | 1.1 | 1.1 | 1.1 | 1.1
Signature: Neil Lebbern | [5 empty] | Date: 09/01/2020

## TNP Verification Report O2
Transitional National Plan Annual Verification Report (V1.0) |  |  |  | TNP YEAR |  | 4 (2019)
Peripheral Species: O2 or H2O (if applicable) | O2 | ELV1: (%) | 6 | LCP: (TNP ref.) |  | 283
Process Operator: RWE Generation UK plc |  |  | Permit No: |  | RP3133LD
Address: Aberthaw Power Station, The Leys, Aberthaw, Near Barry, Vale of Glamorgan, CF62 4ZW |  |  | TNP Contact: |  | Neil Lebbern
|  |  | Tel No: |  | 07584703227
|  |  | Email: |  | neil.lebbern@rwe.com
EN 15259 (Representative Sampling)
EN 15259: (PASS/FAIL) |  |  | Test Date(s):
Non-Compliances: (including stratification factors if applied in addition to QAL2 factors)
QAL1 (Instrument Suitability)
Make/Model: ZFG2 |  |  |  |  | MCERTS: Yes (Y/N) |  | MC 990001/03
Manufacturer: ABB |  |  |  |  | Sample Type2: | In situ
QAL2 (Calibration)3
LCP unit within windshield or Instrument number: | - | Unit 7 | Unit 8 | Unit 9
QAL2 Factors: b (gradient)4 | - | 1.0433 | 1 | 0.9439
a (offset) | % | 0 | 0 | 0
Test date | - | 2019-01-24 | n/a | 2019-01-21
Date applied5 | - | 2019-08-22 | n/a | 2019-08-28
Variability6 | % | 0.0709 |  | 0.1636
VCR from test data7a | % | 13 |  | 12
VCR extended (if applicable)7b | % | n/a |  | n/a
Second QAL2 (Calibration) (if applicable)
QAL2 Factors: b (gradient)4 | -
a (offset) | %
Test date | -
Date applied5 | -
Variability6 | %
VCR from test data7a | %
VCR extended (if applicable)7b | %
AST (Annual Surveillance Test)
LCP units within windshield: | - | Unit 7 | Unit 8 | Unit 9 | Unit 7 | Unit 8 | Unit 9
Test date | -
Variability6 | %
Validity (Mean Deviation)6 | %
VCR extended (if applicable)7c | %
QAL3 (Ongoing Drift Checks)
Frequency8: | Every
Alarm (Action) Limit: | %
Warning Limit: | %
Signature: Neil Lebbern | [5 empty] | Date: 09/01/2020

## TNP Verification Report H2O
Transitional National Plan Annual Verification Report (V1.0) |  |  |  | TNP YEAR |  | 4 (2019)
Peripheral Species: O2 or H2O (if applicable) | H2O | ELV1: (%) | 6 | LCP: (TNP ref.) |  | 283
Process Operator: RWE Generation UK plc |  |  | Permit No: |  | RP3133LD
Address: Aberthaw Power Station, The Leys, Aberthaw, Near Barry, Vale of Glamorgan, CF62 4ZW |  |  | TNP Contact: |  | Neil Lebbern
|  |  | Tel No: |  | 07584703227
|  |  | Email: |  | neil.lebbern@rwe.com
EN 15259 (Representative Sampling)
EN 15259: (PASS/FAIL) |  |  | Test Date(s):
Non-Compliances: (including stratification factors if applied in addition to QAL2 factors)
QAL1 (Instrument Suitability)
Make/Model: Pulsi 200 Series |  |  |  |  | MCERTS: Yes (Y/N) |  | MC990006/07
Manufacturer: Procal |  |  |  |  | Sample Type2: | In situ
QAL2 (Calibration)3
LCP unit within windshield or Instrument number: | - | Unit 7 | Unit 8 | Unit 9
QAL2 Factors: b (gradient)4 | - | 1.083 | 1 | 1.055
a (offset) | % | -1.22 | 0 | -0.75
Test date | - | 2019-01-24 | n/a | 2019-01-21
Date applied5 | - | 2019-08-22 | n/a | 2019-08-28
Variability6 | % | 0.1228 |  | 0.0726
VCR from test data7a | % | 8 |  | 8
VCR extended (if applicable)7b | % | 10 |  | 10
Second QAL2 (Calibration) (if applicable)
QAL2 Factors: b (gradient)4 | -
a (offset) | %
Test date | -
Date applied5 | -
Variability6 | %
VCR from test data7a | %
VCR extended (if applicable)7b | %
AST (Annual Surveillance Test)
LCP units within windshield: | - | Unit 7 | Unit 8 | Unit 9 | Unit 7 | Unit 8 | Unit 9
Test date | -
Variability6 | %
Validity (Mean Deviation)6 | %
VCR extended (if applicable)7c | %
QAL3 (Ongoing Drift Checks)
Frequency8: | Every
Alarm (Action) Limit: | %
Warning Limit: | %
Signature: Neil Lebbern | [5 empty] | Date: 09/01/2020

## TNP Verification Report Flow
Transitional National Plan Annual Verification Report (V1.0) |  |  |  | TNP YEAR |  | 4 (2019)
STACK FLOW |  | ELV1: (m3/s) | 576 | LCP: (TNP ref.) |  | 283
Process Operator: RWE Generation UK plc |  |  | Permit No: |  | RP3133LD
Address:Aberthaw Power Station, The Leys, Aberthaw, Near Barry, Vale of Glamorgan, CF62 4ZW |  |  | TNP Contact: |  | Neil Lebbern
|  |  | Tel No: |  | 07584703227
|  |  | Email: |  | neil.lebbern@rwe.com
EN 15259 (Representative Sampling)9
EN 15259: (PASS/FAIL) |  |  | Test Date(s):
Non-Compliances: (Including stratification factors if applied in addition to QAL2 factors) | N/A, type 2 calibration, pre-investigation has not been performed
QAL1 (Instrument Suitability)
Make/Model: n/a |  |  |  |  | MCERTS: (Y/N) |  | n/a
Manufacturer: n/a |  |  |  |  | Sample Type2: | n/a
QAL2 (Calibration)3
LCP unit within windshield or Instrument number: | - | Unit 7 | Unit 8 | Unit 9
QAL2 Factors: b (gradient)4 | - | 0.98 | 1.03
a (offset) | m3/s | 0 | 0
Test date | - | 2017-03-01 | 2017-11-30
Date applied5 | - | n/a | n/a
Variability6 | m3/s | 5.17 | 8.96
VCR from test data7a | m3/s | 576.46 | 530.85
VCR extended (if applicable)7b | m3/s | n/a | n/a
Second QAL2 (Calibration) (if applicable)
QAL2 Factors: b (gradient)4 | -
a (offset) | m3/s
Test date | -
Date applied5 | -
Variability6 | m3/s
VCR from test data7a | m3/s
VCR extended (if applicable)7b | m3/s
AST (Annual Surveillance Test)
LCP units within windshield: | - | Unit 7 | Unit 8 | Unit 9 | Unit 7 | Unit 8 | Unit 9
Test date | -
Variability6 | m3/s
Validity (Mean Deviation)6 | m3/s
VCR extended (if applicable)7c | m3/s
QAL3 (Ongoing Drift Checks)
Frequency8: | Every
Alarm (Action) Limit: | m3/s
Warning Limit: | m3/s
Signature: Neil Lebbern | [5 empty] | Date: 18/01/2019

## TNP Verification Report Notes
Notes:
1 Specify the Daily Emission Limit Value (ELV) used for QA purposes (this may be a percentile daily ELV for some plant). For plant subject to the JEP Protocol, including power plant, the oxygen ELV is 6% by volume, or 10% for a gas turbine, and the water ELV (if applicable) is 6% by volume. For other plant, the oxygen and water 'ELV' are 21% and 30% by volume respectively, as specified by the Environment Agency in TGN M20 (refer to the most recent version). For flow, specify the surrogate ELV defined in EN ISO 16911-2, i.e., 120% of the maximum flow rate measured during the QAL2 (or 120% of the base load flow if QAL2 data not yet available), noting that the flow reference condition are the actual duct conditions (when flow is measured continuously) or the reporting conditions (when the flow is calculated). The units on the form may be changed to m/s when the flow is measured continuously if this is more appropriate.
2 Sample type. Specify from the following options: In-situ (probe); In-situ (cross-duct); Extractive (hot/wet); Extractive (chiller/dry); Extractive (permeation drier).
3 The QAL2/AST must be compliant with PASS status on Variability/Validity Test as applicable using the current value of the Daily Emission Limit Value (see also Note 6). For oxygen, water vapour and verification of a flow calculation, the QAL2 factors are not usually applied but still enter the QAL2 factors and enter 'N/A' in the 'Date applied'. For verification of a flow calculation the AST Validity test result (mean deviation) must also be reported.
4 If b < 0.90 provide a justification or schedule for repeat testing in the space below.
5 In Year 1 this is 1 Jan 2016; only change the date if a repeat QAL2 is conducted.
6 Variability (scatter) and the average Deviation between the CEM and the Test Laboratory results are defined in EN14181:2014 Section 8.5 (AST) and Section 6.6 (QAL2) and these are reported by the Test Laboratory in the specified concentration or flow units. The Variability and Deviation must be less than pre-defined levels in order to pass.
7a Valid Calibration Range (VCR) is defined in EN14181:2014 Section 6.5 and is reported by the Test Laboratory in the specified concentration or flow units.
7b The VCR may be extended using reference materials by agreement with the Regulatory Authority. Report the most VCR as extended by reference materials here (in addition to the VCR obtained from the test data -see 5a).
7c The VCR may be extended using AST data by up to 50% of the daily ELV. Report the extended VCR from the AST (in addition to the VCR obtained from the test data - see 5a).
8 Specify the frequency of QAL3 checks, e.g., weekly. QAL3 is the control chart approach defined in EN 14181 for monitoring zero and span drift. Two thresholds for monitoring drift are defined - the Warning limit and the Alarm (Action) limit. Action must be taken when the drift exceeds the Action limit. For flow, the units may be changed to reflect the use of a flow surrogate for the QAL3, e.g., % deviation from span.
9 For flow, report the results of the pre-investigation flow survey (if applicable) in the space provided for recording non-compliances. Report the Reproducibility, crest factor and skewness as defined in EN ISO 16911-2.
Justification for QAL2 gradient being less than 0.90 and/or schedule for additional QAL2 testing:
In the above justification, consider the following factors as a minimum requirement. Consult with the Test Laboratory in relation to: the sampling locations for the CEM and the test probes (are these both representative and do they interfere with one another?); uncertainty of the test method (there may be loss of SO2 in test methods that use a chiller to dry the sample for analysis); functional test results for the CEM (has it been set up and checked properly prior to testing?); leakage in either the CEM or the test equipment (compare oxygen levels in the first instance); functional check history (has the instrument performance degraded?).