	Document no:   EMF 005 
	Environmental Management Systems
	Issue no: 1
	Page 1 of 2

	Issue date  07/03/19
	Issued by:  Technical & QA Department

	Link documents: 

	Reason for amendment:  New reporting form
	Authorised by:


[image: image1.png]RADNOR
HILLS





	RADNOR HILLS MINERAL WATER COMPANY

ENVIRONMENTAL MANAGEMENT SYSTEMS

 EMF 005 – NRW SCHEDULE 5 REPORTING FORM




Schedule 5 - Notification
These pages outline the information that the operator must provide.

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.

Part A

	Permit Number
	EPR / AB3697CN

	Name of operator
	Radnor Hills Mineral Water Company Ltd

	Location of Facility
	Radnor Hills, Heartsease, Knighton, Powys, LD7 1LU

	Time and date of the detection
	Detection Reported – 22/01/20


	(a) Notification requirements for any activity that gives rise to an incident or accident which

significantly affects or may significantly affect the environment

	To be notified Immediately

	Date and time of the event
	

	Reference or description of the

location of the event
	

	Description of where any release into the environment took place
	

	Substances(s) potentially released
	

	Best estimate of the quantity or rate of release of substances
	

	Measures taken, or intended to

be taken, to stop any emission
	

	Description of the failure or accident.
	


	(b) Notification requirements for the breach of a permit condition

	To be notified immediately

	Emission point reference/ source
	W1 – Treated effluent discharge

	Parameter(s)
	Orthophosphate PO3−4-P

	Limit
	SRP as P - 0.2mg/l 

	Measured value and uncertainty
	SRP as P - 0.233mg/l

	Date and time of monitoring
	19/01/2020 07:00am

	Measures taken, or intended to

be taken, to stop the emission
	Action 1:

Reduced dosing concentration level of P dosing from 17mg/l to 10mg/l.

Action 2:
Concentration level of biomass MLSS was below operational range. Therefore prohibited wasting of biomass for following day in order to increase MLSS concentration level and improve treatment of effluent.

	Time periods for notification following detection of a breach of a limit

	Parameter
	Notification period

	
	

	
	


	(c) In the event of a breach of permit condition which poses an immediate danger to human health

or threatens to cause an immediate significant adverse effect on the environment:

	To be notified immediately

	Description of where the effect on the environment was detected
	

	Substances(s) detected
	

	Concentrations of substances

detected
	

	Date of monitoring/sampling
	


Part B - to be submitted as soon as practicable

	Any more accurate information on the matters for notification under Part A.
	Performance of the activated sludge for the treatment process has been affected by the following:

The characteristics of the biomass is currently being affected by the seasonal change of temperature. This change has impacted temperature of the biomass, at the start of the week was 16.1°C and reduced to 12.9°C by the end of the week.

The concentration level of SRP within the effluent had significantly risen from an average of 0.2mg/l to 0.5mg/l. An increase which was not positively reduced or treated by the MBR system due to the performance of the activated sludge which had been affected by temperature.



	Measures taken, or intended to be taken, to prevent a recurrence of the incident
	Immediate reduction in P dosing concentration level of P from 17mg/l to 10mg/l. 

Resample taken 19/01/20 after change to nutrient concentration level. Result of Orthophosphate PO3−4 was 0.1mg/l. 


	Measures taken, or intended to be taken, to rectify,

limit or prevent any pollution of the environment which has been or may be caused by the emission
	No discharge to river at present.

	The dates of any unauthorised emissions from the facility in the preceding 24 months.
	26/02/19

24/07/19

12/11/19
07/01/20


	Name*
	

	Post
	

	Signature
	

	Date
	


* authorised to sign on behalf of the operator

