
Schedule 5 - Notification 

These pages outline the information that the operator must provide. 

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the PPC Regulations.

Part A 
	Permit Number
	EPR/BL1096IB/V013

	Name of operator
	Castle Cement Limited

	Location of Installation
	Padeswood Works, Padeswood, Mold.

	Time and date of the detection 
	16/8/2019


	(a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques, accident, or fugitive emission which has caused, is causing or may cause significant pollution

	To be notified within 24 hours of detection

	Date and time of the event
	

	Reference or description of the location of the event 
	

	Description of where any release into the environment took place
	

	Substances(s) potentially released
	

	Best estimate of the quantity or rate of  release of substances
	

	Measures taken, or intended to be taken, to stop any emission
	

	Description of the failure or accident.
	


	(b) Notification requirements for the breach of a limit

	To be notified within 24 hours of detection unless otherwise specified below

	Emission point reference/ source
	Main stack monitor

	Parameter(s)
	NOx

	Limit
	450

	Measured value and uncertainty
	487

	Date and time of monitoring
	15/08/2019 Daily average

	Measures taken, or intended to be taken, to stop the emission
	SNCR system manually increased in an attempt to compensate for the high daily average found on shift handover. Low site air pressure initially prevented the SNCR system from running, this was resolved by 21:00 and system introduced. However the levels of NOx at this point were too high to allow for reduction below 450 by midnight.

	Time periods for notification following detection of a breach of a limit

	Parameter
	Notification period

	
	

	
	

	
	


	(c) Notification requirements for the detection of any significant adverse environmental effect

	To be notified within 24 hours of detection

	Description of where the effect on the environment was detected
	

	Substances(s) detected
	

	Concentrations of substances detected
	

	Date of monitoring/sampling
	


Part B - to be submitted as soon as practicable
	Any more accurate information on the matters for notification under Part A.
	At 16:00 on 15/08/2019 the daily NOx average reading was 395 mg/Nm3 and the instantaneous reading was 300 mg/Nm3. Soon after 16:00 the SNCR system experienced low compressed air pressure and this resulted in loss of flow of ammonia to the calciner.

The low compressed air pressure was investigated and an issue was found with a filter on kiln 4 compressors. Filter 3 (outlet of desiccator) in the compressor room was reading high differential pressure and this was identified as the cause of the low pressure. The bypass valve of the filter was released to allow air to Kiln 4 system.

The ammonia system returned to service at approx. 21:00 but unable to increase the ammonia flow adequately enough to reduce daily average to within permitted limits.

	Measures taken, or intended to be taken, to prevent a recurrence of the incident
	The equipment supplier was immediately contacted to the review what actions had been taken and to inspect the system to prevent a reoccurrence.

During the inspection, the equipment supplier replaced filter 3 and returned the system to normal operating parameters.



	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission
	The equipment supplier replaced filter 3 and returned the system to normal operating parameters.



	The dates of any unauthorised emissions from the installation in the preceding 24 months.
	23/10/2017
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14/01/2018

21/02/2018
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20/03/2018

04/05/2018

16/05/2018

31/05/2018

03/06/2018

16/08/2018
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04/08/2018

16/08/2018

21/08/2019
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05/01/2019

22/03/2019

29/03/2019


	Name*
	Stewart Mitchell

	Post
	Quality & Environment Manager

	Signature
	S. Mitchell


	Date
	24.01.2020


* authorised to sign on behalf of Castle Cement Limited
