[bookmark: _GoBack]Schedule 6 - Notification 
These pages outline the information that the operator must provide. 
Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.
If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the PPC Regulations.
Part A 
	Permit Number
	EPR/BJ9703IM

	Name of operator
	Kimberly-Clark Limited

	Location of Installation
	Coleshill Paper Mill, Aber Road, Flint, Flintshire, CH6 5EX

	Time and date of the detection 
	25/05/2019



	(a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques, accident, or fugitive emission which has caused, is causing or may cause significant pollution

	To be notified within 24 hours of detection

	Date and time of the event
	25/05/2019

	Reference or description of the location of the event 
	Final Discharge point – Kimberly Clark Flint

	Description of where any release into the environment took place
	Discharge into the estuary

	Substances(s) potentially released
	Ammonia

	Best estimate of the quantity or rate of  release of substances
	Total flow of discharge 1174 m3

	Measures taken, or intended to be taken, to stop any emission
	Denitrifying bacteria added to the aeration as art of our shutdown management strategy.  

	Description of the failure or accident.
	Ammonia exceeds IPPC limit of 4mg/l 



	(b) Notification requirements for the breach of a limit

	To be notified within 24 hours of detection unless otherwise specified below

	Emission point reference/ source
	W2

	Parameter(s)
	Ammonia

	Limit
	4 mg/l

	Measured value and uncertainty
	4.88 mg/l

	Date and time of monitoring
	25/05/2019

	Measures taken, or intended to be taken, to stop the emission
	Additional nitrifying bacteria added to the aeration basin.  Final effluent recirculated through the plant prior to discharge.  Splash aerators in use to air strip the ammonia.

	Time periods for notification following detection of a breach of a limit

	Parameter
	Notification period

	Ammonia
	Without delay

	
	

	
	

	(c) Notification requirements for the detection of any significant adverse environmental effect

	To be notified within 24 hours of detection

	Description of where the effect on the environment was detected
	Sample measured from sampler at discharge

	Substances(s) detected
	Ammonia

	Concentrations of substances detected
	4.88mg/l

	Date of monitoring/sampling
	25/05/2019



Part B - to be submitted as soon as practicable
	Any more accurate information on the matters for notification under Part A.
	Information correct as detailed in Part A

	Measures taken, or intended to be taken, to prevent a recurrence of the incident
	 Plant returned to standard following the site shutdown

	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission
	

	The dates of any unauthorised emissions from the installation in the preceding 24 months.
	17/10/2016, 14/02/2017, 08/05/2017, 09/06/2017, 06/11/2017, 24,05,2018, 25/08/2018



	Name*
	Jan Partridge

	Post
	Site Process Engineer Environment and Quality

	Signature
	J. Partridge

	Date
	26/05/2019


* authorised to sign on behalf of Kimberley Clark
