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This report covers the period from 1st January 2019 to 31st December 2019.
The site has one CHP engine: a 1,189KWe Jenbacher CHP. The engines emissions test was carried out in October 2019. All parameters were compliant passed within the required limits.
Gas quality is measured as part of the daily monitoring checks carried out at the plant. The average methane content of the biogas during the reporting period (2019) was 59.6% and this indicates the process is working well and producing a good quality biogas for combustion through the CHP.
The engine ran for a total of 8,467 hours (96.7% availability) during the period. The site also has a standby boiler which is used as a back-up to the engine and to utilise any surplus biogas to supplement heating of the process. The surplus gas burner was utilised for 172 hours which equates to 1.96% of the total available operational hours for the year.   
The site generated a total of 8811.01 MWh compared to 9611.03 MWh (2018); this is the total generation before the parasitic load has been removed. There was a drop in generation due to main degrit work on both digesters which impacted on the ability of the site to process and generate more. 
The plant exported 8121.2 MWH compared to 8821.1 MWH (2018) with a parasitic load of 212.3 MWh, used on site equating to 2.41% of the total generation 
Rainwater is harvested and used within the process and site also has a mains water connection. The total water usage at the facility from the process bund (dirty) and storage bund (clean) for the period are 395m3 and 628.0m3 respectively while 464m3 is the volume of mains water for domestic usage on site.
Bryn Pica continues to maintain its PAS 110, ISO 14001, ISO 9001, OHSAS 18001 standards and Competence management scheme (CMS) V4 standard certification during year 2019; internal and external surveillance audits continue to be regularly carried out.
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