Schedule 5 - Notification 

These pages outline the information that the operator must provide. 

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.

Part A 
	Permit Number
	BJ9681IX

	Name of operator
	Essity UK Ltd Oakenholt Mill.

	Location of Facility
	Chester Road, Oakenholt, Flintshire, CH6 5PU

	Time and date of the detection 
	09/04/2020


	(a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques, accident, or emission of a substance not controlled by an emission limit which has caused, is causing or may cause significant pollution

	To be notified within 24 hours of detection

	Date and time of the event
	

	Reference or description of the location of the event 
	

	Description of where any release into the environment took place
	

	Substances(s) potentially released
	

	Best estimate of the quantity or rate of release of substances
	

	Measures taken, or intended to be taken, to stop any emission
	

	Description of the failure or accident.
	


	(b) Notification requirements for the breach of a limit

	To be notified within 24 hours of detection unless otherwise specified below

	Emission point reference/ source
	W1

	Parameter(s)
	Biological Oxygen Demand & Suspended Solids 

	Limit
	BOD – 25mg/L Suspended Solid – 50mg/L)

	Measured value and uncertainty
	BOD 25.6mg/L (Uncertainty of measurement of 23.6% at a 95% confidence)
Suspended Solids – 56mg/L (Uncertainty of measurement at 11.39%) 

	Date and time of monitoring
	24hr sample relating to period 24/03/2020 12:00:00 – 25/03/2020 12:00:00. 
(Sample taken was sent to external laboratory for BOD analysis and Suspended Solids analysis whose results were received later due to incubation time) 

	Measures taken, or intended to be taken, to stop the emission
	Investigating programme change at buffer tank to smooth out variations in load. 



	Time periods for notification following detection of a breach of a limit

	Parameter
	Notification period

	
	

	
	

	
	


	© Notification requirements for the detection of any significant adverse environmental effect

	To be notified within 24 hours of detection

	Description of where the effect on the environment was detected
	

	Substances(s) detected
	

	Concentrations of substances detected
	

	Date of monitoring/sampling
	


Part B – to be submitted as soon as practicable
	Any more accurate information on the matters for notification under Part A.
	Process team currently investigating cause. Daily suspended solids sample results had returned  back to normal levels, well below the limit, the day after and continues to be below the limit.  

	Measures taken, or intended to be taken, to prevent a recurrence of the incident
	To be decided upon investigation.  

	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission
	See above. 

	The dates of any unauthorised emissions from the facility in the preceding 24 months.
	25/06/2019, 24/04/2019, 31/10/2018, 17/01/2018, 16/03/2018, 09/10/2018, 09/07/2018, 11/02/2020 


	Name*
	Nick Arundell

	Post
	Quality & Environment Engineer 

	Signature
	

	Date
	09/04/2020 


* authorised to sign on behalf of the operator



