Olleco Cymru Wales Permit Number: EPR/BP3296EF

Permit Variation Application – Food Waste Storage and Bulking

Response to Schedule 5 Notice for Additional Information

Introduction

Olleco has submitted an application for a variation to permit number EPR/BP3296EF to extend the permit boundary for the temporary storage of used cooking oils and food waste (Application number: PAN-007602).

Olleco received a Schedule 5 Notice requesting additional information on 3 February 2020. This submission provides the information requested.

Information Requested

  - Storage of waste oils and fats on the extended permit boundary

Please provide the relevant section of your Environmental Management System (EMS) or amend your application to state what procedures you have in place to ensure all the containers are sealed and no leakages or spillages occur.

Olleco work instruction ‘OLL-WI-003 Spillage, Prevention and Dealing with Spillages’ forms part of the Group EMS. This provides instruction to drivers on vehicle checks, inspecting the integrity of containers on collection and during off-loading and how to deal with a spillage of used cooking oil if it should occur. The work instruction is provided in Appendix 1.

Used cooking oil collected by Olleco vehicles is stored in specially designed wheelie bins and smaller containers (plastic barrel, tubs and metal tins). The containers are off loaded at the end of each day and packed onto wooden pallets secured with plastic shrink wrap. The pallets are normally moved to the factory for processing each day. If there is a need to temporarily store used cooking oil overnight, the pallets are moved into the warehouse for safe storage.

Any containers observed to be leaking or in poor condition are quarantined and placed on a spill pallet until an over container is arranged to allow safe transfer to the processing site.

- Site Drainage

Please provide the inspection and maintenance procedures for the drainage systems including the sump, the oil interceptor and the IBC containers. For more information on storage in containers and maintenance of drainage systems refer to our guidance ‘How to comply with your environmental permit’ p. 29 and p.43. 2.2

Please state when the proposed drainage systems will be installed. Please note that these systems must be in place prior to issue of this variation.

The vehicle wash bay will be constructed with perimeter Aco drains, falling to an impermeable concrete collection sump. Every six months the sump will be emptied and cleaned using a jet vac tanker to prevent the build-up of silt. The condition and integrity of the sump will be visually checked after cleaning.

The oil interceptor will be serviced at least every six months, and more frequently if required, to prevent an excess build-up of silt and oil that can affect the operation of the interceptor. Service records will be maintained. Every five years the interceptor will be fully emptied and given a general inspection to test the integrity and performance of the system.

The interceptor will also be fitted with a separator alarm to warn when the level of oil reaches 90% of the oil storage volume indicating that the system is in need of immediate emptying for it to continue to work effectively.

The capital expenditure for the new surfacing and associated drainage works has been approved by the Olleco Board of Directors, however the programme of work has not yet been finalised with the contractors. Olleco therefore request that NRW issue the permit with a pre-operational condition that requires a programme of work for the construction to be agreed prior to the commencement of activities. This would be consistent with the approach taken by the EA and SEPA at other permitted sites operated by Olleco.

IBCs are stored on spill pallets. The condition of IBCs and the spill pallets are formally inspected once per month as part of a site SHE audit which is undertaken by the Regional Safety Adviser. The audits are documented and dates assigned for any corrective actions (see Appendix 2 for the audit template).

- Spill Tray

Please state where the spill tray (to contain any food waste spills) will be washed and how the wash water will be pumped into the IBC container. Please provide this information in the amended EMS.

The spill tray will be washed within the new vehicle wash bay that will be constructed at the rear of the site, adjacent to the food waste trailer storage area. The wash bay will be constructed with perimeter Aco drains, falling to a concrete sump to contain the wash water. This will be periodically pumped out using a submersible pump into an IBC for disposal off site. Management of the sump water will be the responsibility of the Operations Manager.

The Standard Operating Procedure for the food waste bulking trailer (CYM-FW-SOP-001 Goliath Food Compactor Operation) has been amended to specify where the spill tray should be washed down. Please see Appendix 3.

- Site Infrastructure

4.1 Please confirm if the yard area is either an impermeable surface or a permeable surface where water can freely drain though.

The extended yard will be constructed of impermeable reinforced concrete, designed in accordance with BS EN 1992-3:2006 ‘Design of concrete structures. Liquid retaining and containing structures’.

All concrete work will be executed in accordance with BS EN 13670: 2009 ‘Execution of concrete structures’.

4.2 Please confirm when the area that will be used to park the food waste trailer will be installed. Please confirm whether this area will be impermeable or permeable?

The extended yard area will be used to park the food waste trailer and for the vehicle wash bay. The area will be surfaced with impermeable reinforced concrete to the standards detailed above.

The capital expenditure for the new surfacing works has been approved by the Olleco Board of Directors, however the programme of work has not yet been finalised with the contractors. Olleco therefore request that NRW issue the permit with a pre-operational condition that requires a programme of work for the construction to be agreed prior to the commencement of activities. This would be consistent with the approach taken by the EA and SEPA at other permitted sites operated by Olleco.

- Odour

5.1 Please identify ‘abnormal/emergency’ operating conditions that may impact on odour potential and the measures to mitigate them.

No emergency operating conditions are foreseen with respect to the operation of the food waste bulking trailer. However, abnormal operating conditions could arise in the following circumstances.

- Loss of containment

The food waste collected is mainly solid and does not flow. Any spills can be mitigated by the use of a spill tray to collect any spills during tipping. Olleco will ensure that there are adequate spill kits available and that relevant staff are trained in the spill procedure. The rear yard area where the food waste trailer will be stored will be surfaced with good quality concrete.

- Storage of waste

Under normal operating conditions, waste will only be held on site for 24 hours prior to transport to one of Olleco’s two food waste anaerobic digestion plants for processing. In the event that both sites were unavailable or there was a road traffic incident that prevented transport to the area, contingency arrangements will be in place to tip the waste at a third party AD Plant (Asgard Renewables, Cardigan or Geneco, Avonmouth).

- Failure to adhere to housekeeping requirements

It is important that good housekeeping and hygiene are conditions are maintained to prevent odours. As part of the daily odour tour the food waste storage area will be inspected by the Operations Manager and any deficiencies identified.

5.2 Please provide mitigation measures for when accepted waste is very odourous and odour escapes the site boundary. What action will you take if you detect odour or if you receive complaints? What is the threshold of odour intensity for you to take action?

The Plant Supervisor shall be notified following detection of any odour of intensity 2 (faint odour) or above at any of the offsite monitoring points so that further inspection can be undertaken to investigate the source of the odour on site and, if substantiated, to identify any corrective actions.

Complaints are handled in accordance with EMS Procedure 8.2.2 (please see Appendix 4).