Permit Number: EPR/EP3230BW	Operator: EnviroWales Limited Facility:	Rassau Recycling Facility	     Form Number: Sewer1: 15/04/2014
[bookmark: _GoBack]  Reporting of emissions to sewer for the period from 01/01/19 to 31/12/2019
	Emission
Point
	Substance /
Parameter
	Emission
Limit Value
	Reference Period
	Result [1]
	Test
Method [2]
	Sample
Date and Times [3]
	Uncertainty
[4]

	S1
	Flow
	350m3/day
	Daily average
	139.82
	Meter MCERTs
	
	

	S1
	Suspended solids
	400 mg/l
	Weekly average
	7.68
	BS EN 872
	
	

	S1
	Hydrocarbon oil
	No visible staining
	Daily samples
	
	SCA blue book 77
	
	

	S1
	pH max
	11
	-
	9.2
	BS ISO 10523
	
	

	S1
	pH min
	6
	
	7.2
	
	
	

	S1
	Sulphate
	2000 mg/l
	Weekly average
	1009
	SCA blue book 136
	
	

	S1
	Antimony and its compounds (as Sb)
	2.5 mg/l
	Weekly average
	0.03
	BS EN ISO 15586
	
	

	S1
	Arsenic and its compounds (as As)
	2.5 mg/l
	Weekly average
	0.002
	BS EN ISO 11969
	
	

	S1
	Cadmium and its compounds (as Cd)
	0.25 mg/l
	Weekly average
	0.01
	BS EN ISO 5961
	
	

	S1
	Copper and its compounds (as Cu)
	12.5 mg/l
	Weekly average
	0.02
	BS 6068-2.29
	
	

	S1
	Lead and its compounds (as Pb)
	5 mg/l
	Weekly average
	0.03
	BS EN ISO 15586
	
	

	S1
	Mercury and its compounds (as Hg)
	0.125 mg/l
	Weekly average
	0.0022
	BS EN 1483
	
	

	S1
	Nickel and its compounds (as Ni)
	12.5 mg/l
	Weekly average
	0.01
	BS 6068-2.29
	
	

	S1
	Zinc and its compounds (as Zn)
	12.5 mg/l
	Weekly average
	0.03
	BS 6068-2.29
	
	



The result given is the maximum value (or the minimum value in the case of a limit that is expressed as a minimum) obtained during the reporting period, expressed in the same terms as the emission limit value. Where the emission limit value is expressed as a range, the result is given as the ‘minimum – maximum’ measured values.
Where an internationally recognised standard test method is used the reference number is given. Where another method that has been formally agreed with Natural Resources Wales is used, then the appropriate identifier is given. In other cases the principal technique is stated, for example gas chromatography.
For non-continuous measurements the date and time of the sample that produced the result is given. For continuous measurements the percentage of the process operating time covered by the result is given.   
[image: img-Z111032-0001]The uncertainty associated with the quoted result at the 95% confidence interval, unless otherwise stated.

		
Signed        (Authorised to sign as representative of Operator)     Date:31/01/2020
image1.png




