## Sheet1
Submission number | Submission Batch | Permit Number | PAN Reference | Permit Officer | For Action/ For Information | NRW Standard Comments | Detailed Comments | DCWW Operator Review Comments
1240 | January | CG0405901 | PAN-009520 | Gareth |  |  |  | draft agreed. Permit ready for issue.
1241 | January | BW1404301 | PAN-009535 | Gareth | For action | Multiple issues | DCWW submission states 2802 storage but old consent states 2820. Drafted as 2820. Can DCWW confirm the storage capacity? Submission states 10 mm mesh, old consent states 10 mm bar. Drafted with bar. Can DCWW confirm the screening dimensions? | Agreed. Existing Pemrit from 2003 has 2820m of storage & 10mm bar
1242 | January | CM0001202 | PAN-009536 | Sion |  |  |  | draft agreed. Permit ready for issue.
1243 | January | AN0087501 | PAN-009537 | Sion | For action | Multiple issues | Point of discharge changed. Please can DCWW confirm the asset type (CSO or SPS). | This asset is an SPS for Storm and Emergency Overflow.
1244 | January | BP0318001 | PAN-009534 | Sion | For information | Amended screen size to match previous consent |  | draft agreed. Permit ready for issue.
1245 | January | CM0149302 | PAN-009548 | Sion | For action | Screening query | Old consent states that there is a screen however, does not state dimensions. Can DCWW confirm dimensions otherwise we will need to add an improvement condition. Name changed to better reflect asset. | 10mm bar screen, name change is fine.
1246 | January | BP0317301 | PAN-009538 | Sion | For information | Amended screen size to match previous consent |  | draft agreed. Permit ready for issue.
1247 | January | CG0058803 | PAN-009371 | Sion | For action | Multiple issues | Receiving waters seem to be Nant Brysgwll. DCWW submitted Nant Brisgyll. Drafted with Brysgwll. Old consent states 6mm mesh. Drafted with 6mm mesh. Are DCWW happy with the change? | Llanfestiniog STW STORM happy with the change to the receiving water. I can see no mention of 6mm mesh in the current consent but happy with 6mm mesh.
1248 | January | CG0019202 | PAN-009382 | William |  |  |  | draft agreed. Permit ready for issue.
1249 | January | CG0337001 | PAN-009366 | William | For Information | Settled storm permit |  | draft agreed. Permit ready for issue.
1250 | January | CM0058402 | PAN-009621 | Sarah | For action | Multiple issues | Site name amended. New site map produced - no map was provided with the submission so please check and confirm this map and the NGRs are all correct, thanks. | happy with this permit
1251 | January | CG0357401 | PAN-009374 | Sarah | For information | Site name amended |  | draft agreed. Permit ready for issue.
1252 | January | BP0328301 | PAN-009459 | Sarah |  |  |  | draft agreed. Permit ready for issue.
1253 | January | BP0315301 | PAN-009517 | Gareth |  |  |  | draft agreed. Permit ready for issue.
1254 | January | BP0328401 | PAN-009423 | Gareth |  |  |  | draft agreed. Permit ready for issue.
1255 | January | CG0110902 | PAN-009413 | Gareth |  |  |  | draft agreed. Permit ready for issue.
1256 | January | AB0067102 | PAN-009358 | Sarah |  |  |  | draft agreed. Permit ready for issue.
1257 | January | AD0002919 | PAN-009359 | Sarah | For information | Multiple issues | Address details amended and Point of Overflow changed | draft agreed. Permit ready for issue.
1258 | January | CG0114505 | PAN-009363 | Sarah | For action | Multiple issues | Point of Overflow changed. Please could you confirm that the Point of Discharge is correct on the site map? Does the settled storm tank overflow share a discharge point with the final effluent? | Llanerchymedd STW STORM the discharge is at SH 45140 86230 on the Afon Goch but it is a long outfall distant from site and it is shared by the final effluent too. There are other Settled Storm CG0114501 and EO CG0114503 permits closer to site to the Afon Alaw at SH 41700 84410 too though.
1259 | January | CG0179701 | PAN-009364 | Sarah | For action | Multiple issues | Address details amended. Receiving waters changed - appeared to be a small typo (Dollen -> Collen); however, please could you confirm receiving waters is River Collen, as the point of discharge appears to be at the confluence of the Cledwen, Collen and Elwy rivers. | Permit states Afon Collen. Our sewer plan shows that the outfall may be to the Afon Cledwen however lets say it outfalls to the Afon Elwy Wikipedia tells me that the "Elwy is a river in Wales forming a tributary to the River Clwyd. The source of the river is sometimes said to be on the northern flank of Moel Seisiog, south-east of Llanrwst, at Ordnance Survey grid reference SH 853593. However the river only receives the name Elwy at the village of Llangernyw, where three rivers, Afon Cledwen, Afon Collen and Afon Gallen, meet to form the Elwy".Can we please put receiving waters as the River Elwy.
1260 | January | AN0010102 | PAN-009494 | Sarah | For information | Multiple issues | Site name amended and address details amended | draft agreed. Permit ready for issue.
1261 | January | BW0600901 | PAN-009519 | Sarah | For action | Multiple issues | Site name amended and address details amended. Please confirm storage capacity of the wetlands lagoon. As the lagoon is sweetened with final effluent it will always have some liquid in it; does the capacity given in the submission reflect this? | Happy with the name and address changes. The existng permit has a total storage of 2950m. I am not sure I undertand why that is divided up in the new permit. My undertanding is it should remin as per the existing - total storm storage of 2950m
1262 | January | CG0366101 | PAN-009501 | Sarah | For information | Multiple issues | Site name amended and Point of Overflow changed. Improvement condition for screen information included as the 1995 application form gives inflow screening to 6mm. | draft agreed. Permit ready for issue.
1263 | January | CG0428901 | PAN-009492 | Sarah | For information | Site name amended |  | draft agreed. Permit ready for issue.
1264 | January | BP0219401 | PAN-009530 | Sion | For action | See detailed comments | DCWW submitted 10m3 of storage and a 10mm bar screen. The 1991 application form (on our database) states that the storage capacity will be 50.4m3, although this is not stated in the 1991 or 1995 permits. The 2016 Solutions Document - states several things that are of concern: ● The Introduction states that “the works is non-compliant with the Settled Storm consent since flows are unscreened prior to filling the tanks”. ● The Scheme Summary states that the tanks are not functioning well so only have a storage capacity of 31m3 (which supports my above comment that the tanks were intended to have a capacity greater than the 10m3 given in the current submission). ● The incoming flow is macerated not screened – this would immediately make any activity related to the storm sewage discharge non-compliant as all our permits state that the discharge should not be comminuted or macerated. The solutions document, produced in December 2016, made recommendations to improve the asset. Please could you confirm whether these have been put in place? If improvements have been made, please could you confirm that the macerator has been removed and replaced by a 10mm bar screen (as per submission) and that the storage tank has been returned to functioning at its full capacity (and what that capacity is)? Thanks. | This scheme was removed an never built. Therefore existing permit conditions would be transferred to the new permit.
1265 | January | BP0044502 | PAN-009370 | Sarah | For information | New site map produced |  | draft agreed. Permit ready for issue.
1266 | January | BP0345701 | PAN-009362 | Sarah |  |  |  | draft agreed. Permit ready for issue.
1267 | January | CG0081201 | PAN-009357 | Sarah | For information | Multiple issues | Address details amended. Point of Discharge changed. Point of Overflow changed. | draft agreed. Permit ready for issue.
1268 | January | CG0341602 | PAN-009356 | Sarah | For information | Multiple issues | Site name amended. Address details amended. | draft agreed. Permit ready for issue.
1269 | January | CG0075601 | PAN-009521 | Sarah |  |  |  | draft agreed. Permit ready for issue.
1270 | January | AN0391101 | PAN-009656 | Sarah |  |  |  | draft agreed. Permit ready for issue.
1271 | January | CG0134002 | PAN-009474 | William |  |  |  | draft agreed. Permit ready for issue.
1272 | January | BP0341101 | PAN-009385 | William |  |  |  | draft agreed. Permit ready for issue.
1273 | January | CG0415601 | PAN-009445 | Sion |  |  |  | draft agreed. Permit ready for issue.
1274 | January | CM0009501 | PAN-009391 | Sion | For action | See detailed comments | Please can DCWW confirm the asset type (CSO or SPS). | Asset type is CSO
1275 | January | CM0018302 | PAN-009437 | Gareth |  |  |  | draft agreed. Permit ready for issue.
1276 | January | CG0364501 | PAN-009502 | Sion |  |  |  | draft agreed. Permit ready for issue.
1277 | January | BG0011502 | PAN-009490 | Sarah | For information | Multiple issues | Site name amended. Address details amended. | draft agreed. Permit ready for issue.
1278 | January | AN0092201 | PAN-009496 | Sarah | For information | Multiple issues | Site name amended. Address details amended. Point of Discharge changed. Receiving waters changed. | draft agreed. Permit ready for issue.
1279 | January | CG0087502 | PAN-009498 | Sarah | For information | Multiple issues | Site name amended. Address details amended. | draft agreed. Permit ready for issue.
1280 | January | AN0391701 | PAN-009515 | Sarah | For information | Site name amended |  | draft agreed. Permit ready for issue.
1281 | January | AB0038202 | PAN-009497 | Sarah | For information | Site name amended |  | draft agreed. Permit ready for issue.
1282 | January | NPSWQD009506 | PAN-009361 | Sarah |  |  |  | draft agreed. Permit ready for issue.
1283 | January | CG0429001 | PAN-009455 | Tom | For action | Screening query | Drafted with screen because previous consent states there is a 6mm screen. Please could you confirm? | 10mm screen
1284 | January | CG0058303 | PAN-009392 | Tom | For action | Screening query | Drafted with screen because previous consent states there is a 6mm screen. Please could you confirm? | James - Gwalchmai STW STORM. I can see no mention of a screen in the previous consent. 6mm sounds fine SAP says we have a Longwood Escalator screen which come 6mm as standard (3mm as fine)
1285 | January | CG0134102 | PAN-009463 | Gareth | For action | See detailed comments | Previous consent (2005) has storage (>2 hours at 3DWF). Please could DCWW confirm if there is storage at the asset and its capacity, if known? | James - SAP shown no storm storage. Need to check with site and get back to you
1286 | January | NPSWQD005734 | PAN-009444 | Gareth |  |  |  | draft agreed. Permit ready for issue.
1287 | January | BP0339101 | PAN-009412 | Gareth | For action | See detailed comments | A variation was issued in 2015 to increase PFF and storm storage to reflect the current increase in Dry Weather Flow as a result of the increased Population Equivalent within the catchment. The PFF has been increased from 2.4l/s to 4.9l/s and the on-line storm storage capacity has increased from 40m3 to 51.6m. The current submission has the 'old' data. Can DCWW confirm the increased PFF and storage are still relevant? There is a discrepancy between the NGR on the 2015 permit and the current submission. Could DCWW confirm which is correct? | The conditions in the 2015 permit apply (4.9l/s & 50.6m). The new NGR's are correct.
1288 | January | NPSWQD009903 | PAN-009398 | Tom | For information | Site name amended | Amended to include asset type (CSO) | draft agreed. Permit ready for issue.
1289 | January | CG0185101 | PAN-009375 | Tom | For information | Site name amended | Amended to include asset type (CSO) | draft agreed. Permit ready for issue.

## Sheet2
Point of Discharge changed
Point of Overflow changed
Point of Discharge and Point of Overflow changed
New site map produced
Pumping Station permit produced
Weir setting not given in l/s
Potential bathing water
Amended screen size to match previous consent
Address details amended
Potential Shellfish
Multiple issues
Receiving waters changed
Amendment to storage
See detailed comments
Site name amended
Requires pumping station key protection measures
Screening query
Spill trigger permit produced
Amended details to match previous consent
Weir setting changed
Amended from a pumping station to CSO
CSO permit produced
Settled storm permit