CYM-EMS-SOP-007	Sump and Interceptor Maintenance Procedure

Purpose

The purpose of this SOP is to ensure the pump and interceptor are fully maintained and fully operational at all times.

Scope

This SOP applies to Wales Site

Responsibility

Senior operations manager is responsible for the implementation of this procedure and for training colleagues in the procedure.

Procedure

The materials of construction for the containment and pumping of the effluent will be suitable to ensure collection capacities are sufficient and the materials of construction are correct for the materials being handled.( low risk vehicle wash water water).

Every week the interceptor and sump pump will be checked visually to ensure it is operating as normal. This visual check will recorded in record sheet contained in Appendix 1 of this procedure.

The sump pump will be checked serviced on a frequency of every 3 months. To ensure it is always working at its optimal performance. The sump pump operates on a float switch, turning on when the flow into the sump reaches the desired level for operation. The sump will also have a high level alarm installed to warn when the levels reach 90% of the storage volume. All flow to the sump will be stopped if the alarm activates and the reason for the alarm activation investigated and the necessary remedial action taken. A spare pump will be retained on site and the two switched on a 3 monthly frequency to allow the cleaning and servicing to take place.

Every six months the sump will be emptied and cleaned using a jet vac tanker to prevent the build-up of silt. The condition and integrity of the sump will be visually checked after cleaning.

The oil interceptor will be serviced at least every six months, and more frequently if required, to prevent an excess build-up of silt and oil that can affect the operation of the interceptor. Service records will be maintained. Every five years the interceptor will be fully emptied and given a general inspection to test the integrity and performance of the system.

The interceptor will also be fitted with a separator alarm to warn when the level of oil reaches 90% of the oil storage volume indicating that the system is in need of immediate emptying for it to continue to work effectively. The interceptor alarm/level detection will be serviced/checked on a quarterly basis.

All maintenance work will be recorded in the sheet as contained in Appendix 1 of this procedure.

Appendix 1 – Maintenance Records Sheet

EMPLOYEE TRAINING DECLARATION

| Document no.: |  | Related Risk Assessment ID No.(s) |  |
| --- | --- | --- | --- |
| Depot / Location / Area |  | Task / Activity |  |

I have been shown, trained and understand the standard operating procedure of the above task / activity. I agree to follow the SOP documented at all times

I have been made aware of and understand the risks associated with this task and the consequences if this work instruction is not adhered to.

I the trainer have trained the above person in the procedures laid out in this work instruction.  I am satisfied that the person has shown competency in the task/activity/equipment by way of:

| Name | Title | Signature | Trainer | Date |
| --- | --- | --- | --- | --- |