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Notice of variation and consolidation with introductory note
Environmental Permitting (England & Wales) Regulations 2016

RWE Generation UK plc

Pembroke Power Station
West Pennar 
Pembroke
Pembrokeshire
SA71 5SS


Variation application number
EPR/DP3333TA/V004
Permit number
EPR/DP3333TA
Pembroke Power Station 
Permit number EPR/DP3333TA 
Introductory note
This introductory note does not form a part of the notice.
Under the Environmental Permitting (England & Wales) Regulations 2016 (schedule 5, part 1, paragraph 19) a variation may comprise a consolidated permit reflecting the variations and a notice specifying the variations included in that consolidated permit. Schedule 1 of the notice specifies that all the conditions of the permit have been varied and schedule 2 comprises a consolidated permit which reflects the variations being made. 

Permit variation following the publication of the revised Best Available Techniques (BAT) Reference Document (BRef) for Large Combustion Plant (LCP). The associated BAT conclusions to this document were published on 17 August 2017 in the Official Journal of the European Union.

[bookmark: _GoBack]This variation incorporates the changes required by the Industrial Emissions Directive following a statutory review of permits in the Large Combustion Plant sector.  These include the amendment of the wording of several permit conditions relating to notifications, changes to emission limits and monitoring requirements and also includes the addition of a condition relating to a requirement for monitoring requirements and also includes the addition of an improvement condition (IC8) relating to Black Start Operation.  The interpretation section of the permit has also been updated and the opportunity has been taken to consolidate the original permit and subsequent variations.

We are satisfied that the operator will be compliant with the published BAT conclusions which will apply from 17 August 2021. 

The rest of the installation is unchanged and continues to be operated as follows:
[bookmark: _Hlk13037394]The Pembroke Power Station installation is a gas-fired power station, with a total thermal input of 4.2GW. The plant consists of five Combined Cycle Gas Turbines (CCGTs) units which can also be operated in open cycle gas turbine (OCGT) mode. Each unit consists of a gas turbine (Alstom GT26), an air intake and filter house, a generator-transformer, an unfired Heat Recovery Steam Generator (HRSG) and 75m stack. 
The schedules specify the changes made to the permit. Schedule 1 of the notice specifies the conditions that have been varied and Schedule 2 comprises a consolidated permit which reflects the changes being made. 

The status log of a permit sets out the permitting history, including any changes to the permit reference number. 


	Status log of the permit

	Description
	Date
	Comments

	Application EA/EPR/DP3333TA/A001
	25/03/10
	Date on which application was duly made.

	Further information requested
	20/07/10
	Further information requested relating to impacts on conservation sites. 

	Further information received
	30/07/10
	Response to request for further information dated 20/07/10. 

	Further information requested
	04/08/10
	Further information requested relating to consideration of Combined Heat and Power (CHP). 

	Further information received
	17/08/10
	Revised noise receptor drawing.

	Further information requested
	24/08/10
	Further information requested relating to impact on Limestone Coasts of South-West Wales SAC. 

	Further information received
	01/09/10
	Response to request for further information dated 24/08/10 (Limestone Coasts of South-West Wales SAC). 

	Further information received
	03/09/10
	Response to request for further information dated 04/08/10 (CHP).

	Further information received.
	12/10/10
	Noise model input data.

	Further information requested
	22/10/10
	Further information requested relating to noise, impacts on terrestrial habitats, water treatment plant effluent composition and findings in respect of the impact of the proposed cooling water discharge on the Pembrokeshire Marine SAC. 

	Further information received
	12/11/10
	Noise model input data (including national grid references for noise sources)

	Further information received
	16/11/10
	Response to terrestrial habitats, noise and water treatment plant effluent composition elements of request for further information dated 22/10/10 (water treatment plant element subsequently superseded). 

	Further information received
	26/11/10
	Response to elements of request for further information dated 22/10/10 relating to water treatment plant effluent composition and findings in respect of the impact of the proposed cooling water discharge on the Pembrokeshire Marine SAC (water treatment plant element subsequently superseded).

	Further information received
	30/11/10
	NOx conversion information. 

	Further information received
	01/12/10
	NOx conversion and noise information. 

	Further information received
	23/12/10
	HRSG blow-down information.

	Further information requested
	14/01/11
	Further information relating to noise. 

	Further information received
	17/01/11
	First order decay modelling of TRO plume and addendum. 

	Further information received
	28/01/11
	Revised response to water treatment plant composition element of request for further information dated 22/10/10 (subsequently superseded). 


	Further information received
	09/02/11
	Second addendum to first order decay modelling of TRO plume.

	Further information received
	18/02/11
	Revised response to water treatment plant composition element of request for further information dated 22/10/10 (subsequently superseded). 

	Further information received
	08/03/11
	Air quality information

	Further information received
	15/03/11
	Consideration of thermal plume impact on inter-tidal benthos.

	Further information received
	22/03/11
	Consideration of the potential for formation of chlorination by-products and amended permit application documentation (revised Supporting Document for a New Environmental Permit Application). 

	Further information received
	24/03/11
	Further information in respect of sodium hypochlorite dosing of the main cooling water system and drum screens (subsequently superseded). 

	Further information received
	29/03/11
	Information received in respect of inter-cooling and plan received showing pump house drainage detail. Summary of 2011 noise survey data also submitted. 

	Further information received
	11/04/11
	Response to noise further information request dated 14/01/11 (revised noise impact assessment (Chapter 2 of Part II of Volume 2 of the permit application)). This was subsequently superseded. 

	Further information received
	13/04/11
	Section 36 stack height information. Revised drainage plan and plan of air and water release points (incorporating revised installation boundary). Both were subsequently superseded. 

	Further information received
	20/04/11
	Further information received in respect of noise associated with vessels in the Haven. Information also received in respect of plant thermal inputs and accounting for cooling water pump acoustic panels in the modelling of noise emissions. 

	Further information received
	05/05/11
	Revised Appendix 2.3 of permit application (Cooling water system vulnerability to bio-fouling). This has subsequently been superseded. 

	Further information received
	09/05/11
	Further information received in respect of BAT for noise minimisation.

	Further information received
	11/05/11
	Revised plan of air and water release points (showing revised installation boundary), revised plan of site layout and installation boundary, and revised plan of permanent operational drainage (showing revised installation boundary). Further information also received in respect of plant thermal inputs (additional to that previously received).

	Further information received
	17/05/11
	Further information received in relation to nutrients.

	Further information received
	18/05/11
	Further information received in relation to metals and cooling water retention time. 

	Further information received
	27/05/11
	Further information received in respect of noise impact (at Pwllcrochan and Hundleton)

	Further information received
	02/06/11
	Further information received on water quality modelling in response to CEFAS queries.

	Further information received 
	10/06/11
	Revised short- and long-term assessment of nutrient and metal contributions to W1 discharge from HRSG blow-down, water treatment plant and HRSG chemical clean effluent.

	Further information received
	13/06/11
	Further revised response to water treatment plant composition element of request for further information dated 22/10/10 (subsequently superseded). 

	Further information received
	15/06/11
	Further revised Appendix 2.3 of permit application (Cooling water system vulnerability to bio-fouling) and further information on sodium hypochlorite dosing of the main cooling water system and drum screens also received (subsequently superseded). Confirmation of capacity to isolate drum screens received.

	Further information received
	16/06/11
	Further revised noise impact assessment (Chapter 2 of Part II of Volume 2 of the permit application). This supersedes all previous versions. Further revised Appendix 2.3 of permit application (Cooling water system vulnerability to bio-fouling) and further information on sodium hypochlorite dosing of the main cooling water system and drum screens also received (supersedes all previous versions). 

	Further information received
	28/06/11
	Confirmation of the use of hydrofluoric acid in the commissioning process. 

	Further information received
	01/07/11
	Confirmation that all substances have been accounted for in W1 discharge screening document

	Further information received
	07/07/11
	Further revised Supporting Document for a New Environmental Permit Application, revised Chapter 2 of Part 1 of Volume 2 of the permit application and revised Chapter 3 of Part 2 of Volume 2 of the permit application (all amended to include hydrofluoric acid). 

	Further information received
	27/07/11
	Confirmation of TRO dispersion modelling at fixed value of 50µg/l. 

	Further information received
	03/08/11
	Confirmation of approach to screening of water treatment plant emissions


	Further information received
	22/08/11
	Further information in respect of nutrient load

	Further information received
	23/08/11
	Further information in respect of phosphorus, nitrogen and unionised ammonia


	Further information received
	24/08/11
	Further information in respect of phosphorus emissions and effects on eelgrass beds


	Further information requested
	12/09/11
	Further information requested in respect of the effect of nutrient emissions on macro-algal growth, the toxicity of phosphonates and updates to the W1 emissions screening report. 

	Further information received
	13/09/11
	Information regarding mitigation of phosphate emissions

	Further information received
	15/09/11
	Further information regarding mitigation of phosphate emissions

	Further information received
	19/09/11
	Response to further information request dated 12/09/11 regarding assessment of the impact of nutrient emissions on macro-algal growth

	Further information received
	23/09/11
	Response to further information request dated 12/09/11 regarding phosphonates, updated W1 emissions screening report and revised assessment of the impact of nutrient emissions on macro-algal growth

	Further information received
	26/09/11
	Further revised response to further information request dated 12/09/11 regarding assessment of the impact of nutrient emissions on macro-algal growth

	Further information received
	27/09/11
	Response to further information request dated 12/09/11 (MSDS for new anti-scalant)

	Further information received
	29/09/11
	Further revised W1 emissions screening report

	Further information received
	06/10/11
	Further updated W1 emissions screening report

	Further information received
	07/10/11
	Further information regarding mitigation of phosphate emissions

	Further information received
	10/10/11
	Further information regarding mitigation of phosphate emissions

	Further information received
	11/10/11
	Further updated W1 emissions screening report, amended to account for the change in the Applicant’s proposals from dosing with trisodium phosphate to dosing with sodium hydroxide. 

	Application determined
	10/11/11
	Permit issued

	Application EPR/DP3333TA/V002
	Duly made
07/01/13
	Application to vary the permit to include an onsite sewage treatment plant

	Variation determined EPR/DP3333TA/V002
	26/07/13
	Varied permit issued

	Regulation 60 Notice sent to the Operator 
	14/11/14
	Issue of a Notice under Regulation 60(1) of the EPR. Natural Resources Wales initiated review and variation to vary the permit under IED to implement the special provisions for LCP under Chapter III, introducing new Emission Limit Values (ELVs) applicable to LCP, referred to in Article 30(2) and set out in Annex V. The permit is also updated to modern conditions. 

	Regulation 60 Notice response
	30/03/15
	Response received from the Operator.

	Additional information received
	30/07/15
	Response to request for further information (RFI) dated 08/06/15.

	Variation determined EPR/DP3333TA/V003
	22/12/2015
	Varied and consolidated permit issued in modern condition format. 
Variation effective from 01/01/2016.

	Regulation 61 Notice sent to the Operator
	10/05/2018
	Issue of a Notice under Regulation 61(1)of the EPR. Natural Resources Wales initiated review and variation to vary the permit introduce new Emission Limit Values (ELVs) following the publication of the revised Best Available Techniques (BAT) Reference Document (BRef) for Large Combustion Plants (LCP).

	Regulation 61 Notice response
	16/11/2018
	Response received from the Operator.

	Additional information received
	28/08/2019
	Response to request for further information (RFI) dated 10/06/2019

	Variation determined EPR/DP3333TA/V004
	02/07/2020
	Varied and consolidated permit issued in modern condition format. 
Variation effective from 02/07/2020



	Other Part A installation permits relating to this installation

	Operator
	Permit number
	Date of issue

	RWE Generation UK plc
	GB-EA-ETCO2-1399 (EU ETS permit)
	12/02/08

	RWE Generation UK plc
	22/61/6/156 (abstraction licence)
	03/02/09

	RWE Generation UK plc
	EPR/HP3820XU (water discharge activity permit pertaining to site drainage)
	14/06/11



End of introductory note
Notice of variation and consolidation
The Environmental Permitting (England and Wales) Regulations 2016
The Natural Resources Body for Wales (“Natural Resources Wales”) in exercise of its powers under regulation 20 of the Environmental Permitting (England and Wales) Regulations 2016 varies and consolidates
Permit number
EPR/DP3333TA
Issued to
RWE Generation UK plc (“the operator”)
whose registered office is
Windmill Hill Business Park
Whitehill Way
Swindon
Wiltshire
SN5 6PB 
company registration number 03892782 
to operate a regulated facility at
Pembroke Power Station
West Pennar
Pembroke
Pembrokeshire
SA71 5SS
to the extent set out in the schedules.
The notice shall take effect from 02/07/2020

	Name
	Date

	
Holly Noble

	
02/07/2020





Authorised on behalf of Natural Resources Wales

Schedule 1
[bookmark: _Hlk13039247]All conditions have been varied by the consolidated permit as a result of a Natural Resources Wales initiated variation.

Schedule 2 – consolidated permit
Consolidated permit issued as a separate document.
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