## Schedule 5 Notification

These pages outline the information that the operator must provide.

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.

Part A

| Permit Number | EPR/AB3092CV |
| --- | --- |
| Name of operator | Parc Adfer Operations Limited |
| Location of Facility | Parc Adfer Energy Recovery Facility Deeside |
| Time and date of the detection | 20th August 2020 at 10:30hrs |

| (a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques, accident, or emission of a substance not controlled by an emission limit which has caused, is causing or may cause significant pollution |  |
| --- | --- |
| To be notified within 24 hours of detection |  |
| Date and time of the event | 20th August 2020 at 10:30hrs |
| Reference or description of the location of the event | Lime spillage occurred during the transfer of lime powder from road tanker to the site lime storage silo located in the Flue Gas Treatment area. Lime from the silo top also fell to site roadway below. No emission beyond site building and roadway / hardstanding areas. |
| Description of where any release into the environment took place | Flue Gas Treatment area |
| Substances(s) potentially released | Lime powder |
| Best estimate of the quantity or rate of release of substances | 200kg directly onto silo roof and surrounding walkways |
| Measures taken, or intended to be taken, to stop any emission | Delivery terminated Spill Contained Area cleaned down |
| Description of the failure or accident. | Indications of radio interference with silo monitoring and alarms. Under further investigation prior to submitting Part B. |

| (b) Notification requirements for the breach of a limit |  |
| --- | --- |
| To be notified within 24 hours of detection unless otherwise specified below |  |
| Emission point reference/ source | Lime storage silo |
| Parameter(s) | Kg |
| Limit | None specified |
| Measured value and uncertainty | n/a |
| Date and time of monitoring | n/a |
| Measures taken, or intended to be taken, to stop the emission | Review of delivery contro9ls |

| Time periods for notification following detection of a breach of a limit |  |
| --- | --- |
| Parameter | Notification period |

| (c) Notification requirements for the detection of any significant adverse environmental effect |  |
| --- | --- |
| To be notified within 24 hours of detection |  |
| Description of where the effect on the environment was detected | No effect on the environment detected |
| Substances(s) detected | Lime powder |
| Concentrations of substances detected | N/A |
| Date of monitoring/sampling | N/A |

Part B - to be submitted as soon as practicable

| Any more accurate information on the matters for notification under Part A. | The silo High Level alarm would trip the fill process as normal but the use of the simulated level had been initiated due to blinding of the silo level giving a false reading during silo filling and not reset. The practice had been instigated by CNIM and not disables post hand over. The communication of the status of this simulation was not passed on between operations teams at hand over nor recorded in the shift log. Status of the simulation was not passed on the Plant Management |
| --- | --- |
| Measures taken, or intended to be taken, to prevent a recurrence of the incident | Level alarm simulation only to be utilised on the obtaining of specific permission from the Plant Manager. Briefing note to go to all Ops personnel to this effect Lime silo level sensor and transmitter to be serviced at the September 2020 outage. Investigation by CNIM into radio interference with alarms in the FGT area. |
| Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission | No environmental damage detected Attenuation pond monitored and the initial rise in pH was monitored until it returned to normal levels before any releases took place. |
| The dates of any unauthorised emissions from the facility in the preceding 24 months. | 28th January 2020 8th February 2020 20th February 2020 23rd March 2020 11:30 to 11:59hrs 23rd March 2020 15:00 to 15:29hrs 7th April 21:00am to 21.29am 8th April 00:20am to 0.29am 8th April 10:00am to 10.29am 21st April 2020 at 15:00hrs to 15:29hrs 1st May 2020 at 07:49hrs 1st May 2020 at 14:09hrs 3rd May 2020 CO 15:00 to 15:29hrs140.92mg/Nm³. 30th May 2020 CO 15:00 to 15:29hrs 110.16mg/Nm³. 26th June 2020 CO 06:10 to 06:19hrs of 152.23mg/Nm³. 13th August 2020 CO 15:00 hrs to 15:29 hrs of 108.52 mg/Nm³. |

| Name* | Jonathan Farebrother |
| --- | --- |
| Post | Plant Manager |
| Signature |  |
| Date | 20/08/2020 |

* authorised to sign on behalf of the operator