Permit Reference Number: VP3339PD					Operator: Morganite Electrical Carbon Ltd

Installation: Electrical Carbon Swansea				Form Number: A1

# Reporting of Emissions to Air for the period from	January ’20	to	December ‘20;		January ’20	to	March ‘20

| Emissions to Air |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Emission Point | Substance / Parameter | Emission # Limit Value (mg/m3) | Result [1] | Test Method [2] | Sample Date and Times [3] | Accreditation/Certification [4] | Uncertainty (mg/m3) [5] |
| A10 | Lead | 2 | 0.051 | BS EN 14385:2004 | 10:55 – 11:57; 22/01/2020 | UKAS/MCERTS | 0.051 |
| A10 | Copper | 2 | 0.585 | BS EN 14385:2004 | 10:55 – 11:57; 22/01/2020 | UKAS/MCERTS | 0.085 |
| A10 | Antimony | 2 | 0.001 | BS EN 14385:2004 | 10:55 – 11:57; 22/01/2020 | UKAS/MCERTS | 0.0001 |
| A10 | Lead | 2 |  | BS EN 14385:2004 |  | UKAS/MCERTS |  |
| A10 | Copper | 2 |  | BS EN 14385:2004 |  | UKAS/MCERTS |  |
| A10 | Antimony | 2 |  | BS EN 14385:2004 |  | UKAS/MCERTS |  |
| A10 | Lead | 2 |  | BS EN 14385:2004 |  | UKAS/MCERTS |  |
| A10 | Copper | 2 |  | BS EN 14385:2004 |  | UKAS/MCERTS |  |
| A10 | Antimony | 2 |  | BS EN 14385:2004 |  | UKAS/MCERTS |  |
| A10 | Lead | 2 |  | BS EN 14385:2004 |  | UKAS/MCERTS |  |
| A10 | Copper | 2 |  | BS EN 14385:2004 |  | UKAS/MCERTS |  |
| A10 | Antimony | 2 |  | BS EN 14385:2004 |  | UKAS/MCERTS |  |
| A27 | Sulphur dioxide | 2900 |  | BS ISO 7935:1992 |  | UKAS/MCERTS |  |
| A28 | Sulphur dioxide | 2900 |  | BS ISO 7935:1992 |  | UKAS/MCERTS |  |
| A61 | Sulphur dioxide | 2900 |  | BS ISO 7935:1992 |  | UKAS/MCERTS |  |
| A27 | Oxides of nitrogen (as NO2) | 150 |  | BS ISO 14792:2005 |  | UKAS/MCERTS |  |
| A28 | Oxides of nitrogen (as NO2) | 150 |  | BS ISO 14792:2005 |  | UKAS/MCERTS |  |
| A61 | Oxides of nitrogen (as NO2) | 150 |  | BS ISO 14792:2005 |  | UKAS/MCERTS |  |
| A10 | Total particulate | 10 | 3.1 | BS ISO 13284:2002 | 09:45 – 10:47; 22/01/2020 | UKAS/MCERTS | 0.66 |
| A15 | Total particulate | 10 |  | BS ISO 13284:2002 |  | UKAS/MCERTS |  |
| A19 | Total particulate | 10 |  | BS ISO 13284:2002 |  | UKAS/MCERTS |  |
| A27 | Total particulate | 10 |  | BS ISO 13284:2002 |  | UKAS/MCERTS |  |
| A28 | Total particulate | 10 |  | BS ISO 13284:2002 |  | UKAS/MCERTS |  |
| A61 | Total particulate | 10 |  | BS ISO 13284:2002 |  | UKAS/MCERTS |  |

[1] The result given is the maximum value (or the minimum value in the case of a limit that is expressed as a minimum) obtained during the reporting period, expressed in the same terms as the emission limit value. Where the emission limit value is expressed as a range, the result is given as the ‘minimum – maximum’ measured values.

[2] Where an internationally recognised standard test method is used the reference number is given. Where another method that has been formally agreed with the Agency is used, then the appropriate identifier is given. In other cases the principal technique is stated, e.g. gas chromatography.

[3] For non-continuous measurements the date and time of the sample that produced the result is given. For continuous measurements the percentage of the process operating time covered by the result is given.

[4] The accreditation status of the equipment and/or the monitoring organisation, as appropriate, for the methods used for both sampling and analysis.

[5] The uncertainty associated with the quoted result at the 95% confidence interval, unless otherwise stated. The following uncertainties are quoted on a different basis (basis as stated) – {The basis of any other uncertainty figure needs to be stated. Where no figure is available the Agency will need to agree an appropriate uncertainty value.}

Signed ……Mark Williamson………………………………  		Date…20/02/2020..…

(Authorised to sign as representative of the Operator)