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	Permit Number:
	NRWWIA173 

	Applicant name:
	DCWW

	Site Address:
	Talybont reservoir, Brecon Beacons national park


	Discharge Point NGR:
	SO 10555 20455

	Respond by date:
	02/10/2019

	Permitting Officer:
	William Wallace



Brief Description of proposal:

DCWW have recently installed new washout valves at Talybont dam and as part of the commissioning process, the valves are required to operate at their full range from closed to open. This will result in a discharge of 17,000,000 litres of water into the Caerfanell river. Please find the application form on the DMS here

Two of the valves are located at the bottom of the Draw off and Scour main which will result in water that contains suspended solids. DCWW have mitigations in place to keep the sediment volume to an acceptable level. Mitigation measures have been taken from a previous application please find them saved on the DMS here

DCWW Currently holds a discharge consent to operate the scour mains twice annually as part of the requirement for silt is managed in the Dam and the emergency drawdown provisions remain operational.

The Discharge rate shall not exceed 2.1 m3/s and the total and daily discharge volume of 17,000,000 litres. 


Habitats Screening Report – Designations or protected species/habitats:
The discharge is directly into the below sites, Conservation please let us know if you would like an appendix 4 assessment or a HRA 

SSSI-AFON WYSG (Isasfonudd)/ River Usk (tributaries)
SAC- AFON WYSG (Isasfonudd)/ River Usk (tributaries)

Risk Assessment Results (modelling or L1 Risk Assessment):



Miscellaneous:

N/A

NRM Responses:

Environment Management comments:
[bookmark: _GoBack]The discharge will be made via the stilling basin which is designed to retain silt, therefore I don’t anticipate a problem with silt in the Caerfanell. I spoke to Owain Sheppard in Hydrology to get an idea of what the maximum flows would look like and he reassured me that they would not be excessive.


Officers name: Simon Worrall
Date: 02/10/2019

Biodiversity comments:


Officers name:
Date:

Fisheries comments:


Officers name:
Date:

Conservation/Ecology Comments:

I think it is correct that NRW Completes a Habitat Regulations Assessment, unless one was done that covers very similar circumstances for the previous case mentioned. Note that since Welsh Water is a Competent Authority they should have undertaken and HRA assessment themselves and provided that to NRW with their application. Dusitaporn Thomas is the appropriate contact.


Officers name:Ken Perry, Senior Environment Officer
Date: 1/10/19

Internal Consultation Responses from other NRW Teams:


Water Quality Planning:


N/A
Officers name:
Date:



Geoscience Response:

N/A


Officers name:
Date:

Flood Risk Management:


N/A

Officers name:
Date:


	External Consultations sent to:
	Yes/No

	National Parks
	N/A

	Water Company regarding Drinking Water Protected Zone / SPZ1
	N/A

	Environmental Heath
	N/A




Any Permitting Responses:








Date:
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