	Document no:   EMF 005 
	Environmental Management Systems
	Issue no: 1.1
	Page 1 of 2

	Issue date: 07/03/20
	Issued by:  Technical & QA Department

	Link documents: EMS 013

	Reason for amendment:  Annual Review, second permit added.
	Authorised by:


[image: image1.png]




	RADNOR HILLS MINERAL WATER COMPANY

ENVIRONMENTAL MANAGEMENT SYSTEMS

 EMF 005 – NRW SCHEDULE 5 REPORTING FORM




Schedule 5 - Notification
These pages outline the information that the operator must provide.

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet, and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.

Part A

	Permit Number
	EPR / AB3697CN – (Emissions to Air and Water) 
or 
EPR / BB3298CT – (Wetland Treatment System)
(Highlight the applicable permit)

	Name of operator
	Radnor Hills Mineral Water Company Ltd

	Location of Facility
	Radnor Hills, Heartsease, Knighton, Powys, LD7 1LU

	Time and date of the detection
	Detection Reported 12/10/20


	(a) Notification requirements for any activity that gives rise to an incident or accident which

significantly affects or may significantly affect the environment

	To be notified Immediately

	Date and time of the event
	

	Reference or description of the

location of the event
	 

	Description of where any release into the environment took place
	

	Substances(s) potentially released
	

	Best estimate of the quantity or rate of release of substances
	

	Measures taken, or intended to

be taken, to stop any emission
	

	Description of the failure or accident.
	


	(b) Notification requirements for the breach of a permit condition

	To be notified immediately

	Emission point reference/ source
	W1 – Treated effluent discharge

	Parameter(s)
	BOD

	Limit
	5.00mg/l

	Measured value and uncertainty
	7.5mg/l

	Date and time of monitoring
	Sample obtained 10:00 24th November. Result reported and received 2nd December

	Measures taken, or intended to

be taken, to stop the emission
	Action 1:

Enquired with the lab to ensure the concentration level of the sample is a true result as continued previous samples have had the level be <5mg/l.

Action 2: 
Resample taken 01/12/20 and sent for external BOD analysis as routine and pending results will be reviewed to ensure the breach has not continued and now stopped.

Action 3:
Resample taken BOD conducted internally analysis completed result 7.0mg/l
Action 4:

Investigation conducted to determine cause of increase.

	Time periods for notification following detection of a breach of a limit

	Parameter
	Notification period

	
	

	
	


	(c) In the event of a breach of permit condition which poses an immediate danger to human health

or threatens to cause an immediate significant adverse effect on the environment:

	To be notified immediately

	Description of where the effect on the environment was detected
	

	Substances(s) detected
	

	Concentrations of substances

detected
	

	Date of monitoring/sampling
	


Part B - to be submitted as soon as practicable

	Any more accurate information on the matters for notification under Part A.
	Weekly samples sent to lab as per our test schedule.

Internal BOD test kit used to conduct analysis and have result sooner. Concentration level similar to results reported by external lab.
External Lab

1st BOD Breach on 24/11/20 – 7.5mg/l
2nd BOD Breach on 01/12/20 – 7.44mg/l

3rd BOD Breach on 08/12/20 – <10mg/l

By week 51 BOD concentration had return within consent limit:

BOD result on 16/12/20 – 4.96mg/l



	Measures taken, or intended to be taken, to prevent a recurrence of the incident
	External lab confirmed that the test results were valid, and all procedures were conducted correctly.


	Measures taken, or intended to be taken, to rectify,

limit or prevent any pollution of the environment which has been or may be caused by the emission
	No discharge to river at present.
Investigation conducted concluded that BOD increase may be caused due to operational changes made to dissolved oxygen system of the MBR. Bioreactor tank dissolved oxygen setpoint reduced November 18th. The decision for reducing setpoint was made to conserve energy as ambient temperatures drop cold liquids can hold more dissolved oxygen. 
Although D.O levels had been satisfactory the increase in effluent COD had not been anticipated and was also a factor to high BOD concentration levels. The operational setpoint of D.O was increased November 30th, reviewed weekly and increased incrementally until BOD results were back within permit level.


	The dates of any unauthorised emissions from the facility in the preceding 24 months.
	26/02/19

24/07/19

12/11/19
07/01/20


	Name*
	R Isaac

	Post
	[image: image2.png]RADNOR
HILLS



Technical & Quality Manager

	Signature
	

	Date
	29/12/20


* authorised to sign on behalf of the operator

