| Permit Number: | PAN-012552 |
| --- | --- |
| Applicant name: | Dyfed & Powys Police |
| Site Address: | Dyfed Powys Air Support Unit Pembrey Helicopter Support Unit Building Pembrey Burry Port SA16 0HZ |
| Discharge Point NGR: | SN 40879 03420 |
| Respond by date: | 24/03/2021 (10 working days) |
| Permitting Officer: | Tara Al-Far |

Brief Description of proposal:

Permit application for a new water discharge activity consisting of treated domestic effluent & Kennel wash down. The system will comprise of a PTP and storage tank discharging a maximum volume of 13 m3/day to Swan Pool Drain via a surface water drain. Swan Pool Drain flows north and terminates in the Gwendraeth estuary which forms part of the Pembrey Coast SSSI. The applicant has confirmed that all solid waste from the kennels will be removed from the site prior to treatment in the PTP and there will be no Toxocara canis in the untreated washdown waste.

Habitats Screening Report – Designations or protected species/habitats:

A risk screening report can be found here.

Whilst the Risk screening report identified one designated SSSI (Gwernydd Penbre) within the 1000-meter screening criteria, the flow of the receiving watercourse is in the opposite direction. Therefore, the proposal is not hydrologically connected to the SSSI and there is no impact pathway. As a result, no Appendix 4 has been completed for this site. Please see file note regarding Appendix 4, saved on the DMS, for further information.

Risk Assessment Results (modelling or L1 Risk Assessment):

I have conducted river quality modelling using RQP which concludes the following:

BOD

The proposed discharge will cause a 0.44% deterioration in the 90%ile BOD concentration immediately downstream of the discharge point at the British Standard treatment efficiency (20mg/l). In line with our current guidance ‘Operational Instruction 50_12 Water Quality Planning: No Deterioration and the Water Framework Directive’, this discharge satisfies the <10% deterioration and will not change the status class of the waterbody.

Ammonia

The proposed discharge will cause a 1.42% deterioration in the 90%ile ammonia concentration immediately downstream of the discharge point at the British Standard treatment efficiency (20mg/l). In line with our current guidance ‘Operational Instruction 50_12 Water Quality Planning: No Deterioration and the Water Framework Directive’, this discharge satisfies the <10% deterioration and will not change the status class of the waterbody.

Miscellaneous:

N/A

Environment Team Responses:

Environment Officer comments:

Officers name:
Date:

Biodiversity comments:

Officers name:
Date:

Fisheries comments:

Officers name:
Date:

Conservation/Ecology Comments:

Officers name:
Date:

Internal Consultation Responses from other NRW Teams:

Water Quality Planning:

Officers name:

Date:

Geoscience Response:

N/A

Officers name:
Date:

Flood Risk Management:

Any works in, over, under of within 16m from Swanpool Drain may require a Flood Risk Activity Permit (FRAP) from NRW under the Environmental Permitting Regulations (2016). Please contact the Development and Flood Risk Team to discuss further DFRSouthPermitting@cyfoethnaturiolcymru.gov.uk.

Officers name: Rachel Thomas
Date: 15.03.21

| External Consultations sent to: | Yes/No |
| --- | --- |
| National Parks | N |
| Water Company regarding Drinking Water Protected Zone / SPZ1 | N |
| Environmental Heath | N |

Any Permitting Responses:

Date: