Schedule 5 - Notification

These pages outline the information that the operator must provide.

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

#### If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the PPC Regulations.

Part A

| Permit Number | EPR/BJ9703IM |
| --- | --- |
| Name of operator | Kimberly-Clark Limited |
| Location of Installation | Flint Paper Mill, Aber Road, Flint, Flintshire, CH6 5EX |
| Time and date of the detection | 04/05/2021 at 06:54 |

| (a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques, accident, or fugitive emission which has caused, is causing or may cause significant pollution |  |
| --- | --- |
| To be notified within 24 hours of detection |  |
| Date and time of the event | 04/05/2021 at 6:54 |
| Reference or description of the location of the event | Leak identified in the effluent discharge pipeline |
| Description of where any release into the environment took place | On Kc site prior to the discharge pipework leaving site. Treated water mainly flowed back into wastewater treatment plant via the on-site drains. A small quantity entered the surface drain which discharges to Flint lake which flows into the same network as the discharge would have taken. |
| Substances(s) potentially released | Final treated wastewater |
| Best estimate of the quantity or rate of release of substances | Approx:100 m3 |
| Measures taken, or intended to be taken, to stop any emission | Discharge pump out stopped immediately and work to excavate pipe and inspect commenced. |
| Description of the failure or accident. | Pipework leak |

| (b) Notification requirements for the breach of a limit |  |  |
| --- | --- | --- |
| To be notified within 24 hours of detection unless otherwise specified below |  |  |
| Emission point reference/ source | W2 |  |
| Parameter(s) | All |  |
| Limit |  |  |
| Measured value and uncertainty | Not measured |  |
| 04/05/2020 at 6:54 | 04/05/2021 at 6:54 |  |
| Measures taken, or intended to be taken, to stop the emission | Leak contained on site. Investigation as to the place / nature of the leak commenced. Area will need to be excavated to identify the pipe damage and repair. |  |
| Time periods for notification following detection of a breach of a limit |  |  |  |
| Parameter |  |  | Notification period |
| (c) Notification requirements for the detection of any significant adverse environmental effect |  |  |
| To be notified within 24 hours of detection |  |  |
| Description of where the effect on the environment was detected | Leak of final effluent to ground prior to discharge from site |  |
| Substances(s) detected | Final treated effluent |  |
| Concentrations of substances detected |  |  |
| Date of monitoring/sampling | 04/05/2021 at 6:54 |  |

Part B - to be submitted as soon as practicable

| Any more accurate information on the matters for notification under Part A. | Pipe excavated and pipe hole and crack identified |
| --- | --- |
| Measures taken, or intended to be taken, to prevent a recurrence of the incident | Pipework repaired and returned to standard. Pipe tested on the first available discharge and no further issues identified |
| Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission |  |
| The dates of any unauthorised emissions from the installation in the preceding 24 months. | 25/05/2019, 05/09/2019, 26/03/2020, 17/04/2020, 13/11/2020 |

| Name* | Jan Partridge |
| --- | --- |
| Post | Flint Site Environment and Energy leader |
| Signature |  |
| Date | 07/05/2021 |

* authorised to sign on behalf of Kimberly Clark