Schedule 1 - Notification of abnormal emissions

Part A 
	Permit Number
	EPR/WP3836ZF

	Name of Operator
	Tradebe Healthcare National Ltd

	Location of Installation
	Wrexham Clinical Waste Incinerator, Marlborough Road, Wrexham Industrial Estate, Wrexham LL13 9RJ

	Location of the emission
	Main stack

	Time and date of the emission
	29th March 21 08.00-22.30


	Substance(s) emitted
	Media
	Best estimate of the quantity or the rate of emission
	Time during which the emission took place

	SO2
	Air
	Daily ELV 171.38
	0800-22.30 raised levels 


	Measures taken, or intended to be taken, to stop the emission
	High readings of SO2 were observed from 08.00hrs – 22.30hrs

4 bins of Gypsum were burned during 06.00-08.00 which took the daily ELV of SO2 – 171.38mg/m3.
Check of abatement system concluded normal operation.

Stopped loading waste during out of range emissions.

Allowed emissions to reduce under normal half hourly levels prior to resuming normal waste loading pattern.




Part B
	Any more accurate information on the matters for notification under Part A.
	All plant functioning normally. 

A normal mix of HTI waste stream was being processed 

4 bins of gypsum got loaded into the incinerator between 6 and 8 am  



	Measures taken, or intended to be taken, to prevent a recurrence of the incident
	A trial was held during 14-16th March in which the ash box temperature was reduced to 800-850 deg and Gypsum was fed through the plant. On all 3 days all emissions remained in limits.
For known Gypsum treatment plant parameters are to be set at an ash box temperature of 800-850 degs

These details however had not been passed from the Regional Operations Manager to the Team Leaders and so the ash box temperature was not checked before the gypsum was loaded 29st Marc


	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment or harm which has been or may be caused by the emission
	Given the lack of consistency when processing Gypsum at the Wrexham plant a decision was made to stop the waste being brought to site for process in bulk volumes. The two main producers we no longer take any waste in from. NHS Scotland is the other main producer and they are looking for an alternative solution themselves.
In small volumes we can process it and as such will accept it from some our smaller producers if they have no alternative.

	The dates of any unauthorised emissions from the Installation in the preceding 24 months.


	29th January 2021 – SO2 breach

8th January 2021 – SO2 breach

September 2020 – SO2 breach
Feb 2020 – Mercury breach

	Name*
	Janine Scott 

	Post
	Site Manager 

	Signature
	J Scott 

	Date
	13th May 21


* authorised to sign on behalf of Tradebe Healthcare National 
