| Permit Number: | PAN-005141 | Operator: | Newbridge Energy Limited |
| --- | --- | --- | --- |
| Facility: | Ruthin | Form Number: | Air1 / 17/12/19 |

Reporting of emissions to air for the period from 17/12/2019 to 09/02/2021

| Emission Point | Substance / Parameter | Emission Limit Value* | Reference Period | Result [1] | Test Method [2] | Sample Date and Times [3] | Uncertainty [4] |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Biomass CHP Plant Exhaust | Oxides of nitrogen (NO and NO2 expressed as NO2) | 475 mg/m3 | Periodic (average over one hour) | 340 | MCERTS BS EN 14792 | 08/02/2021, 21:15 – 22:15. | ±14.3 mg/m3 |
|  | Dust (Particulate matter) | 50 mg/Nm3 |  | 18.6 | MCERTS BS EN 13284-1 | 09/02/2021, 14:04 – 14:34, 14:35 – 15:35. | ±1.4 mg/m3 |
|  | Carbon Monoxide | 225 mg/Nm3 |  | 23.3 | MCERTS BS EN 15058 | 08/02/2021, 21:15 – 22:15. | ±1.5mg/m3 |
|  | TVOC | 30 mg/Nm3 |  | 9.9 | MCERTS BS EN 12619 | 08/02/2021, 21:15 – 22:15. | ±0.88 mg/m3 |

* At reference conditions of a temperature of 273.15 K, a pressure of 101.3 kPa and after correction for the water vapour content of the waste gases at a standardised O2 content of 6% for solid fuel fired boilers

- The result given is the maximum value (or the minimum value in the case of a limit that is expressed as a minimum) obtained during the reporting period, expressed in the same terms as the emission limit value. Where the emission limit value is expressed as a range, the result is given as the ‘minimum – maximum’ measured values.

- Where an internationally recognised standard test method is used the reference number is given. Where another method that has been formally agreed with Natural Resources Wales is used, then the appropriate identifier is given. In other cases the principal technique is stated, for example gas chromatography.

- For non-continuous measurements the date and time of the sample that produced the result is given. For continuous measurements  the percentage of the process operating time covered by the result is given.

- The uncertainty associated with the quoted result at the 95% confidence interval, unless otherwise stated.