Schedule 5 - Notification 
[bookmark: _GoBack]These pages outline the information that the operator must provide. 
Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.
If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.
Part A 
	Permit Number
	GP3235GH

	Name of operator
	Randall Parker Foods

	Location of Facility
	Dolwen Abattoir

	Time and date of the detection 
	21/01/21 13:00



	(a) Notification requirements for any activity that gives rise to an incident or accident which significantly affects or may significantly affect the environment

	To be notified Immediately

	[bookmark: _Hlk452464078]Date and time of the event
	21/01/21 13:00

	Reference or description of the location of the event 
	Chiller 9

	Description of where any release into the environment took place
	Chiller 9 plant room 

	Substances(s) potentially released
	R448A (N40)

	Best estimate of the quantity or rate of  release of substances
	17kg

	Measures taken, or intended to be taken, to stop any emission
	[bookmark: _Hlk452464100][bookmark: _Hlk455555953] Border Temperature control discovered in  routine monitoring found a problem with chill 9 System at 13:00 on the 21/04/21 and immediately turned the unit off.  He checked and replaced the capillary line . The line  was fixed. The condenser was refilled with 17kg R448A (N40)  after 17kg R448A (N40)   was released.

	Description of the failure or accident.
	Leak on condenser  



	(b) Notification requirements for the breach of a permit condition

	To be notified immediately

	Emission point reference/ source
	Chiller 9 Condenser 

	Parameter(s)
	

	Limit
	

	Measured value and uncertainty
	

	Date and time of monitoring
	

	Measures taken, or intended to be taken, to stop the emission
	He checked and replaced the capillary line . The line  was fixed. The condenser was refilled with 17kg R448A (N40)  after 17kg R448A (N40)   was released.



	Time periods for notification following detection of a breach of a limit

	Parameter
	Notification period

	
	

	
	



	(c) In the event of a breach of permit condition which poses an immediate danger to human health or threatens to cause an immediate significant adverse effect on the environment:

	To be notified immediately

	Description of where the effect on the environment was detected
	

	Substances(s) detected
	

	Concentrations of substances detected
	

	Date of monitoring/sampling
	


Part B - to be submitted as soon as practicable
	Any more accurate information on the matters for notification under Part A.
	Gas loss measured and found  to be 

	
	He checked and replaced the capillary line . The line  was fixed. The condenser was refilled with 17kg R448A (N40)  after 17kg R448A (N40)   was released.

	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission
	Border Temperature  to continue to monitor  and carry out preventative maintenance if needed and monitor for leaks 

	The dates of any unauthorised emissions from the facility in the preceding 24 months.
	03/10/2016,3 and 4/12/2016
10/01/17, 17/01/17    /  22/02/17/ 14/03/17,16-07-17,18-08-17,6:11:17
17/1/18  08/02/18 9/5/18 15/08/2018 12/09/2018
19/06/19  04/07/19  04/10/19 20/11/19
11/02/20 21/02/20 29/4/20 05/4/20 15/5/20 22/05/20  31/05/2020 24/06/20  22/7/20 17/08/20 19/08/20, 11/09/2020, 30/09/2020, 18/11/20, 29/11/2020
20/01/2021




	Name*
	Gareth Gower

	Post
	Technical Manager 

	Signature
	

	Date
	22/04/2021


* authorised to sign on behalf of the operator
