These pages outline the information that the operator must provide.

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

#### If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.

Part A

| Permit Number | GP3235GH |
| --- | --- |
| Name of operator | Randall Parker Foods |
| Location of Facility | Dolwen Abattoir |
| Time and date of the detection | 21/01/21 13:00 |

| (a) Notification requirements for any activity that gives rise to an incident or accident which significantly affects or may significantly affect the environment |  |
| --- | --- |
| To be notified Immediately |  |
| Date and time of the event | 21/01/21 13:00 |
| Reference or description of the location of the event | Chiller 9 |
| Description of where any release into the environment took place | Chiller 9 plant room |
| Substances(s) potentially released | R448A (N40) |
| Best estimate of the quantity or rate of release of substances | 17kg |
| Measures taken, or intended to be taken, to stop any emission | Border Temperature control discovered in routine monitoring found a problem with chill 9 System at 13:00 on the 21/04/21 and immediately turned the unit off. He checked and replaced the capillary line . The line was fixed. The condenser was refilled with 17kg R448A (N40) after 17kg R448A (N40) was released. |
| Description of the failure or accident. | Leak on condenser |

| (b) Notification requirements for the breach of a permit condition |  |
| --- | --- |
| To be notified immediately |  |
| Emission point reference/ source | Chiller 9 Condenser |
| Parameter(s) |  |
| Limit |  |
| Measured value and uncertainty |  |
| Date and time of monitoring |  |
| Measures taken, or intended to be taken, to stop the emission | He checked and replaced the capillary line . The line was fixed. The condenser was refilled with 17kg R448A (N40) after 17kg R448A (N40) was released. |

| Time periods for notification following detection of a breach of a limit |  |
| --- | --- |
| Parameter | Notification period |

| (c) In the event of a breach of permit condition which poses an immediate danger to human health or threatens to cause an immediate significant adverse effect on the environment: |  |
| --- | --- |
| To be notified immediately |  |
| Description of where the effect on the environment was detected |  |
| Substances(s) detected |  |
| Concentrations of substances detected |  |
| Date of monitoring/sampling |  |

Part B - to be submitted as soon as practicable

| Any more accurate information on the matters for notification under Part A. | Gas loss measured and found to be |
| --- | --- |
|  | He checked and replaced the capillary line . The line was fixed. The condenser was refilled with 17kg R448A (N40) after 17kg R448A (N40) was released. |
| Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission | Border Temperature to continue to monitor and carry out preventative maintenance if needed and monitor for leaks |
| The dates of any unauthorised emissions from the facility in the preceding 24 months. | 03/10/2016,3 and 4/12/2016 10/01/17, 17/01/17 / 22/02/17/ 14/03/17,16-07-17,18-08-17,6:11:17 17/1/18 08/02/18 9/5/18 15/08/2018 12/09/2018 19/06/19 04/07/19 04/10/19 20/11/19 11/02/20 21/02/20 29/4/20 05/4/20 15/5/20 22/05/20 31/05/2020 24/06/20 22/7/20 17/08/20 19/08/20, 11/09/2020, 30/09/2020, 18/11/20, 29/11/2020 20/01/2021 |

| Name* | Gareth Gower |
| --- | --- |
| Post | Technical Manager |
| Signature |  |
| Date | 22/04/2021 |

* authorised to sign on behalf of the operator