These pages outline the information that the operator must provide.

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

#### If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.

Part A

| Permit Number | GP3235GH |
| --- | --- |
| Name of operator | Randall Parker Foods |
| Location of Facility | Dolwen Abattoir |
| Time and date of the detection | 14/05/21 16:00 |

| (a) Notification requirements for any activity that gives rise to an incident or accident which significantly affects or may significantly affect the environment |  |
| --- | --- |
| To be notified Immediately |  |
| Date and time of the event | 14/05/21 16:00 |
| Reference or description of the location of the event | Offal room |
| Description of where any release into the environment took place | Offal room evaporator unit |
| Substances(s) potentially released | R448A (N40) |
| Best estimate of the quantity or rate of release of substances | 5kg |
| Measures taken, or intended to be taken, to stop any emission | Border Temperature control discovered in routine monitoring found a problem with offal room System at 16:00 on the 14/05/21 and immediately turned the unit off. He checked and replaced the evaporator unit expansion valve. The condenser was refilled with 5kg R448A (N40) after 5kg R448A (N40) was released. Tested and okay. |
| Description of the failure or accident. | Leak on evaporator unit expansion valve |

| (b) Notification requirements for the breach of a permit condition |  |
| --- | --- |
| To be notified immediately |  |
| Emission point reference/ source | Chiller 3 evaporator unit expansion valve |
| Parameter(s) |  |
| Limit |  |
| Measured value and uncertainty |  |
| Date and time of monitoring |  |
| Measures taken, or intended to be taken, to stop the emission | He checked and replaced the evaporator unit expansion valve. The condenser was refilled with 5kg R448A (N40) after 5kg R448A (N40) was released. Tested and okay. |

| Time periods for notification following detection of a breach of a limit |  |
| --- | --- |
| Parameter | Notification period |

| (c) In the event of a breach of permit condition which poses an immediate danger to human health or threatens to cause an immediate significant adverse effect on the environment: |  |
| --- | --- |
| To be notified immediately |  |
| Description of where the effect on the environment was detected |  |
| Substances(s) detected |  |
| Concentrations of substances detected |  |
| Date of monitoring/sampling |  |

Part B - to be submitted as soon as practicable

| Any more accurate information on the matters for notification under Part A. | Gas loss measured and found to be 5kg R448A (N40) |
| --- | --- |
|  | He checked and replaced the evaporator unit expansion valve. The condenser was refilled with 5kg R448A (N40) after 5kg R448A (N40) was released. Tested and okay. |
| Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission | Border Temperature to continue to monitor and carry out preventative maintenance if needed and monitor for leaks |
| The dates of any unauthorised emissions from the facility in the preceding 24 months. | 03/10/2016,3 and 4/12/2016 10/01/17, 17/01/17 / 22/02/17/ 14/03/17,16-07-17,18-08-17,6:11:17 17/1/18 08/02/18 9/5/18 15/08/2018 12/09/2018 19/06/19 04/07/19 04/10/19 20/11/19 11/02/20 21/02/20 29/4/20 05/4/20 15/5/20 22/05/20 31/05/2020 24/06/20 22/7/20 17/08/20 19/08/20, 11/09/2020, 30/09/2020, 18/11/20, 29/11/2020 20/01/2021, 22/04/2021 26/04/2021 |

| Name* | Gareth Gower |
| --- | --- |
| Post | Technical Manager |
| Signature |  |
| Date | 17/05/2021 |

* authorised to sign on behalf of the operator