# Natural Resources Wales permitting decisions

# Bespoke permit

We have decided to grant the permit for Abbey Consols Metal Mine operated by Natural Resources Wales.

The application number is PAN-014116

The permit number is EPR/CB3292HL

The permit regulates a maximum discharge of 3456 cubic metres per day of

treated minewater from Abbey Consols minewater treatment system. The untreated minewater will pass through an on-site passive sodium carbonate treatment system, which has been proven to successfully remove ~80-90% of zinc from the minewater. The system is comprised of a dosing unit (including store for sodium carbonate powder, dosing tanks and dosing pump), two treatment lagoons with pH sensors to control sodium carbonate dosing, facilities to filter, dry and store metal carbonate sludge and a wetland for post treatment polishing and mixing with clean run-off from the capped areas. The treated minewater will then drain into the River Teifi via a new outfall.

The minewater originates from the abandoned Abbey Consols lead/zinc mine which is the largest source of zinc to the River Teifi (SAC & SSSI), causing it to fail Water Framework Directive standards for at least 14km downstream. This remediation scheme will contribute significantly to the reduction of metal pollution in the receiving watercourse. We consider in reaching that decision we have taken into account all relevant considerations and legal requirements and that the permit will ensure that the appropriate level of environmental protection is provided.

Purpose of this document

This decision document:

- explains how the application has been determined

- provides a record of the decision-making process

- shows how all relevant factors have been taken into account

- justifies the specific conditions in the permit other than those in our generic permit template.

Unless the decision document specifies otherwise we have accepted the applicant’s proposals.

Structure of this document

- Annex 1 the decision checklist

# Annex 1: decision checklist

This checklist should be read in conjunction with the Duly Making checklist.

| ### Aspect | ### Justification / Detail | Criteria met |
| --- | --- | --- |
|  |  | Yes |
| Consultation |  |  |  |
| Scope of consultation | The consultation requirements were identified and implemented. The decision was taken in accordance with RGN 6 High Profile Sites, our Public Participation Statement and our Working Together Agreements. | ü |
| ### Responses to consultation and web publicising | The web publicising and consultation responses were taken into account in the decision. No responses were received from web publicising. The decision was taken in accordance with our guidance. | ü |
| Operator |  |  |  |
| Control of the facility | We are satisfied that the applicant (now the operator) is the person who will have control over the operation of the facility after the grant of the permit. The decision was taken in accordance with EPR RGN 1 Understanding the meaning of operator. | ü |
| European Directives |  |  |  |
| Applicable directives | All applicable European directives have been considered in the determination of the application. | ü |
| The site |  |  |  |
| Extent of the site of the facility | The operator has provided a plan which we consider is satisfactory, showing the extent of the site of the facility including discharge points. A plan is included in the permit and the operator is required to carry on the permitted activities within the site boundary. | ü |
| Biodiversity, Heritage, Landscape and Nature Conservation and a designated site under the Wildlife and Countryside Act. | The application is within the relevant distance criteria of a site of heritage, landscape or nature conservation, and/or protected species or habitat . A full assessment of the application and its potential to affect the [site/species/habitat] has been carried out as part of the permitting process. We consider that the application will not affect the [features of the site/species/habitat] We have not formally consulted on the application. The decision was taken in accordance with our guidance. | ü |
| Habitat Regulation Assessment for a designated site under the EU Habitats Directive | Appropriate assessment: In light of the conclusions of an appropriate assessment, and taking account of the advice received from protected sites advisors, it has been established that the project will not adversely affect the integrity of any Natura 2000/Ramsar site, taking into account any conditions or restrictions as applicable, either alone or in-combination with other plans and projects. (As documented in section 4 of OGN 200 form 1, and section 5 if applicable) Form 1, 2 & 4 – saved on DMS as “to be assessed” for public register purposes. HRA Overall conclusion: In light of the conclusions of the appropriate assessment, it has not been ascertained that the project will not adversely affect the integrity of any Natura 2000/Ramsar site, as documented in section 4 of OGN 200 form 1, and section 5 is applicable. |  |
| Environmental Risk Assessment and operating techniques |  |  |  |
| Environmental risk | We have reviewed the operator's assessment of the environmental risk from the facility. The operator’s risk assessment is satisfactory. The assessment shows that, applying the conservative criteria in our guidance on Environmental Risk Assessment or similar methodology supplied by the operator and reviewed by ourselves, all emissions may be categorised as environmentally insignificant. As a result of the significant environmental improvements to water quality made by providing mine water treatment at this site it has been decided that a descriptive permit will be used to regulate the discharge. As the proposal will aid in the delivery of WFD objectives, H1 screening is not applicable in this case and no further WFD assessment has been completed. | ü |
| Operating techniques | We have reviewed the techniques used by the operator and compared these with the relevant guidance notes. The proposed techniques / emission levels for priorities for control are in line with the benchmark levels contained in the TGN and we consider them to represent appropriate techniques for the facility. | ü |
| The permit conditions |  |  |  |
| Considerations of foul sewer | We agree with the operators justification for not connecting to foul sewer. | ü |
| Operator Competence |  |  |  |
| Environment Management System | There is no known reason to consider that the operator will not have the management systems to enable it to comply with the permit conditions. The decision was taken in accordance with RGN 5 on Operator Competence. | ü |
| Sustainable Management of Natural Resources (SMNR) |  |  |
| Considerations of SMNR - Compliance with our General Purpose | We are satisfied that this decision is compatible with our general purpose of pursuing the sustainable management of natural resources in relation to Wales and applying the principles of sustainable management of natural resources” | ü |
| Environment Wales Act 2016 |  |  |
| Biodiversity and resilience of ecosystems duty | Section 6 of the Environment Wales Act 2016 requires that we seek to maintain and enhance biodiversity in the exercise of our functions, and in so doing promote the resilience of ecosystems, in a manner that is consistent with the proper exercise of our functions. NRW is satisfied that in this case, (in our separate and distinct capacities as applicant and determining body,) we have taken into account and had due regard to this duty in so far as it is consistent with the function of determining an application for a stand alone water discharge activity permit under EPR2016. | ü |