Fire Prevention & Mitigation Plan

| Report compiled by: | Gareth Danter-Hill | Environmental Focus Ltd |
| --- | --- | --- |
| Customer: |  | S L Recycling Ltd |
| Requirement: | Fire Prevention & Mitigation Plan | Variation application |
| Date of Submission: | October 2021 |  |
| Signature: |  | Gareth Danter-Hill |
| Version number and date: | First Version | October 2021 |

Copyright Disclaimer

All material on the pages within this report is the property of Environmental Focus Ltd. Any reproduction of the material in any form is only permitted with full written authorisation. The report and its contents are for the use at the location outlined within the document

and for the named client only.

This document has been prepared in good faith with care and diligence, based on information provided by the client or known to be available at the time. The document fully satisfies the agreed work profile.

Introduction

This FPMP has been prepared in accordance with National Resources Wales Fire Prevention and Mitigation Plan Guidance-Waste Management New Guidance Note 16 version 2 August 2017. Reference has also been made to the Waste Industry Safety and Health Forum document entitled Reducing Fire Risk at Waste Management Sites, issue 2, April 2017.

The Site

The Site is located on the Pontyfelin Industrial Estate approximately 3km south of Pontypool Town centre. The Site neighbours are mixed industrial use land to the north, the A4042 dual carriageway to the west, the Newport Road to the south and the River Afon Lwyd valley to the east. The nearest residential properties are on the eastern side of the Afon Lwyd valley circa 60 m east of the Site.

A Site of Importance for Nature Conservation (SINC), the Pontyfelin verge and ditch, is located within 50m of the boundary of the Site. A non-statutory site, it comprises of species rich marshy and neutral grassland and shrub that provides good connectivity for otters. A further SINC, the river Afon Lwyd is located less than 100m from the Site.

The Site formerly housed a High Temperature Incineration plant operated by Shanks Waste Management Ltd. under a permit issued originally by the Environment Agency. Operations ceased in 2003 and the Site has been progressively decommissioned, demolished and cleared during the intervening years. SL Recycling acquired the Site and have been operating as a non-hazardous waste transfer station and a facility for metal recycling and authorised depollution of used vehicles since July 2019.

Fire Prevention Objectives – Outline Methodology

The purpose of this FPMP is to ensure that all reasonable measures are undertaken to prevent a fire.

The FPMP has been prepared in accordance with National Resources Wales issued Fire Prevention and Mitigation Plan (FPMP) Guidance version 2, issued August 2017. It provides a plan to minimise the likelihood of fire breaking out, a means of extinguishing fire if it broke out, and a statement of methods designed to minimise the spread of fire.

Overarching Management Responsibility

The Site Manager has the responsibility for ensuring that the potential for fire outbreak arising from operations on the Site is minimised. Adequate staffing levels is maintained at all times to ensure the effective operation of the facilities.

In line with current industry best practice, the fire prevention controls set out in the sections below are used as the ‘appropriate measures’ to minimise the risk of and, wherever possible, prevent outbreak of fire associated with Site operations at Unit 1, Pontyfelin Industrial Estate, New Inn, Pontypool, NP4 0DQ.

METHODS AND PROCEDURES TO MAINTAIN COMPLIANCE

Site meetings are held regularly, i.e. during monthly Health and Safety meetings, for Site management to discuss current and planned Site operations with respect to their potential for generating fire and accordingly the FPMP is updated as necessary. Identified actions arising from the meetings and responsibilities for their completion is recorded within the meeting minutes prior to circulation within SL Recycling Limited to the relevant personnel.

Additional and more frequent reviews of the FPMP will be carried out to reflect any changes to operations on-Site and in circumstances that warrant the requirement. Such instances include but are not limited to: an increase in waste quantities accepted on-Site, specifically combustible materials; after any fire incidents in order to make improvements if required; any development made on-Site such as modifications to existing buildings or the incorporation of new infrastructure and/or the installation of new equipment or plant.

The FPMP is a live, working document which is made readily available and clearly identified on Site and all staff are aware of the location of the plan. It is referenced in the Environmental Management System (EMS) and there is a requirement that all contractors working on Site are briefed on the contents of the FPMP.

Briefing for visitors and contractors will include the provision of the correct safety and fire prevention procedures to be carried out in the event of a fire. This involves ensuring they are aware of the information in Section 8 ‘Fire incident and Procedures – Emergency Plan’. In addition, the locations of fire extinguishers and the assembly point will be pointed out.

All staff receive training, which includes on-Site fire drills, with regards to the measures and procedures outlined in the FPMP refresher training is conducted quarterly. New employees will receive inductions which will involve the same training with records of all training maintained to ensure refresher courses are carried out as scheduled. Reference should be made to Section 8 ‘Fire incident and Procedures – Emergency Plan’.

Regular Fire Prevention Plan Exercises are carried out quarterly. The frequency of exercises will be reviewed and changed depending on the results of exercises, reviews of incidents and near misses and the turnover of staff.

SITE PROCESS DESCRIPTION

WASTE ACCEPTANCE

Currently the waste transfer station accepts up to 35,000 tonnes of non-hazardous household commercial and industrial waste per annum and the metal recycling and vehicle storage, depollution and dismantling facility a further 25,000 tonnes of waste metal (of which less than 2,500 tonnes a year is waste motor vehicles). In addition, the amount of wood wastes accepted on-Site does not exceed 11,000 tonnes per annum. All waste streams arise predominantly from the local area and are delivered predominantly by HGVs and vans.

Materials brought to waste transfer station are processed within 2 weeks for general mixed household, commercial and industrial wastes and 1 month for all remaining waste types and, when fully operational, up to 50 tonnes per day of material is brought to Site. Continuous separation of and where necessary, removal off Site of up to 100 tonnes per day of waste within a maximum of one month ensures a regular turnover of material in the waste transfer station. This operational practice mitigates against the development of hot spots.

Drawing No SLR_site_layout shows the layout of the Site facilities, operational areas, stockpile dimensions and Environmental Permit boundary.

SITE ACTIVITIES

The waste transfer station enclosure incorporates a vehicle entry point for the deposition of household waste. The enclosure is constructed with Legato L8 blocks to either side to a height of 4m with openings to the front and rear to ensure the `first in, first out` principle is adhered to. Installed on top of the walls is a bespoke fabric waste management shelter manufactured from polyethylene non-corrosive cladding.

A banksman instructs lorry drivers to reverse into the enclosure for off-loading. Non-Recyclables are removed whilst the load is being tipped and transferred to an authorised energy for waste facility. The remaining materials are sorted and separated within the confines of the enclosure before the transfer to the relevant waste bay on the Site.

Upon deposition of all wastes and during the sorting process, should any batteries be located, they will be removed and stored in the enclosed skip used for battery storage which has the capacity of 2,106 litres (2.106 m3). It is positioned as such to enable easy access should there be a fire within it or if there is a requirement for its removal off-Site/to the quarantine area. Any items likely to contain batteries or a battery unit will be inspected for their presence and, if any are found, they will be stored in an enclosed lidded container as outlined above.

Household, commercial and industrial wastes for recovery or disposal off-Site are manually sorted or with the aid of plant if required, separated and bulked up whilst all bulking of non-hazardous wastes is carried out internally within the waste transfer station enclosure.

Metal recycling involves the sorting, separation, grading, shredding, shearing, compacting, granulating of cables and cutting (using only hand-held equipment) of ferrous metals or alloys and non-ferrous metals for recovery. Pre-sorting also enables the detection of any tramp metals which are removed and stored in an enclosed skip. Storage and recovery of waste motor vehicles takes place on Site in a designated bay with treatment comprising of dismantling and depollution only.

End of Life Vehicles are received via the weighbridge, where they are inspected for quality and contamination prior to transferal to designated depollution bays. These bays are fitted with interceptor drainage systems to eliminate the possibility of ground contamination. On receipt of the vehicle, inspections are initially made for the presence of batteries. If any are installed, they will be disconnected and removed as a matter of priority to the dedicated enclosed skip on-Site. The motor vehicles are manually depolluted.

Separate bays constructed with Legato LG8 blocks are used for the storage of wood and metal. Fully sealed skips are also used for storing batteries and metal filings as per types listed in Table 1. All containers are stored externally on an impermeable concrete pavement, which drains to surface water lagoon, via a 3-stage petrol/oil interceptor. The base and side walls of the lagoon are lined with an impermeable plastic liner.

Hazardous wastes from vehicle depollution are stored and dispatched in separate areas of the Site, or in separate containers as appropriate to avoid mixing of the two. The Operator is aware that under the Hazardous Waste (England and Wales) Regulations 2005, Regulation 18 prohibits the mixing of hazardous waste with non-hazardous waste.

Lead acid batteries are sorted and separated from other wastes but are not treated. They are stored in an enclosed skip, with acid resistant base and a cover to prevent rainwater ingress. The maximum quantity of hazardous waste treated for disposal or recovery does not exceed 10 tonnes per day whilst the maximum quantity stored at one time does not exceed 50 tonnes. This does not include end of life vehicles awaiting depollution. No more than 25 tonnes of intact waste vehicle tyres are stored on Site at any one time.

The waste transfer station enclosure has an impermeable base and is surrounded by a kerbed area, which drains by gravity to the lagoon, via the interceptor. The kerbed area is aligned with the Site boundary, which incorporates the enclosure. The purpose of the design is to ensure that rainwater and any inadvertent liquors or fire water (in the unlikely event of a fire) are fully contained and drained to the lined lagoon.

There is a pre-existing building on the on-Site which housed the laboratory of the previous company. An area to the back of the building is used to store cardboard in a free stack with the dimensions of 5m x 10m x 3m. A line is painted across the side and back of the wall at 3m to ensure the stockpile does not exceed this height.

Access is gained via the one-way internal road to the back of the building which has no rear wall therefore the entire side of the building is open. It is constructed internally of bricks whilst the external walls are cladded. It also houses two fire extinguishers drainage mats for the covering of the adjacent drains for the containment of firewater. Drawing SLR_site_layout shows the locations.

Wood wastes listed in Appendix 1 are stored securely in the designated bay shown on the appended Drawing, where it is also sorted and separated for recovery purposes. Quantities of waste stored does not exceed 10,000 tonnes in total at any one time and no more than 185,000 tonnes will be accepted at the Site over a yearly period. No waste is stored for longer than one month.

No substances that would be classified as ‘dangerous’ under the Control of Major Accident Hazards (COMAH) Regulations are used at the Site for the operation of the facility. There are no cylinders or gas cylinders in use or stored on the Site.

environmental setting

Surface Water / Rivers

There is one main river, the Afon Lwyd, which generally flows parallel to the east of the perimeter at a distance of circa 40-50m. Surface water run-off from the Site is discharged to a holding lagoon situated at the southeast corner of the Site with water tankered off-Site as required to the local wastewater treatment facility.

There are no surface water abstractions likely to be affected by this Site.

Groundwater

The British Geological Survey (BGS) maps state that the Site solid geology bedrock are sediments comprising mudstones siltstones and sandstones of the Raglan Marl group (http://mapapps.bgs.ac.uk/geologyofbritain/home.html). This solid-strata is overlain by alluvial deposits of silts clays and sandstones.

In hydrogeological terms, the underlying strata is classed as a minor aquifer. There are no groundwater abstractions likely to be affected by the Site.

designated sites

Although there are no Environmental Designated Sites within 500m of the Site, there are seven areas designated by Torfaen District Council as non-statutory Sites, Sites of Importance for Nature Conservation (SINC); details are outlined below and includes the SINC name/Grid ref/distance/habitat:

Pont-y-felin verge & ditch (196).  Grid ref: 302986. Distance 50m. Species rich marshy/neutral grassland & scrub – good connectivity for otters.

Butchers Wood (183).  Grid ref: ST297985. Distance 250m.  Wet woodland/ancient woodland.

Butchers grassland (194). Grid ref: ST297985. Distance 380m.  Neutral grassland/ancient woodland.

Craig Y Felin field (67). Grid ref: ST300983. Distance 320m.  Species rich neutral/marshy grassland.

Pont-Y-Felin rush pasture (120). Grid ref: SO302984. Distance 150m. Rush pasture, species poor flora overall, richer along the edges.

Craig Y Felin wood (98). Grid ref: ST301980. Distance 450m.  Ancient woodland, partially replanted.

Afon Lwyd (195). Grid ref: ST302986. Distance <100m.  TCBC watercourse.

At the closest extent, the Llandegfedd Reservoir, designated as a Site of Special Scientific Interest (SSSI), is located 1497m to the north-east of the Site`s boundary.

Air Quality and Prevailing Winds

The Site does not lie in a designated Air Quality Management Zone. According to DEFRA’s Background Air Pollution Mapping Data, 2020, background emission concentrations in the locality of the Site are 9.08µg/m3 and 10.79µg/m3 for NO2 and PM10 respectively. National air quality objectives and European Directive limits and target values stipulate that concentrations of PM10 measured at 24-hour mean levels should not exceed 50 µg/m3 for more than 35 times a year. NO2 concentrations should not exceed 40µg/m3 when measured on an annual mean basis. Based on background concentrations, the air quality in the vicinity of the Site is unlikely to exceed these parameters.

Statistics based on observations taken from the nearest weather station at Llanfrechfa, (c. 20 km south-east of the Site) between April 2012 and September 2020 indicate that, although the prevailing winds are variable, they originate predominantly from the west-south-west with an average speed of 4 knots. The rose diagram in Diagram 4 is conducive of this showing the wind strength distribution and direction also chiefly from the W-S-W. (see Diagram 1).  Data obtained from https://www.windfinder.com/windstatistics/llanfrechfa

Diagram 1  Average Prevailing Wind Direction and Speed

- Diagram 2  Rose Diagram showing Wind Strength Distribution and Direction

Sensitive Receptors

A review of potentially sensitive receptors within a 1km radius of the Site has been undertaken using the hierarchy of hospitals, schools, childcare facilities, elderly housing and convalescent facilities i.e. areas where inhabitants are more vulnerable to the adverse effects of exposure to smoke. Food manufacturers, major infrastructure and protected sites such as SSSIs, SPAs and SCAs are also considered, see Table 1 and Figure 1. Residential properties are considered separately, their locations are detailed in Table 2 and Figure 2.

In terms of predicted exposure risk, levels have been determined via a qualitative assessment which evaluates the likelihood of exposure to smoke emissions based on the receptors’ proximity to the Site and the location of the sensitive receptors with regards to the prevailing wind direction as shown in Figure 1 above.

A 1km radius has been applied as it reflects the maximum potential distance that smoke could reasonably be expected to cause affects in extreme meteorological conditions without any mitigation measures in place. A summary of the identified potentially sensitive receptors within this range along with the overall exposure levels and principal receptor features has been tabulated in Table 1. For each receptor within the categories the determination of the overall risk classification has been based on the dominant risk level.

Within a 1km radii of the Site, no protected sites such as SSSI`s, SAC, SPA or RAMSAR have been identified.

- Table 1   Representative Sensitive Receptors (excluding residential properties). (Reference Point refers to locations on Figure 1)

| Receptor Hierarchy | Facility and Reference Point | Distance and Direction from Site (m) | Overall exposure level | Comments |
| --- | --- | --- | --- | --- |
| Medical Facilities | New Inn Medical Centre (1) | 974 NE | Low | Although located downwind of the dominant prevailing wind it is considered remote from the Site. Pathways are also restricted by intervening infrastructures, trees and hedgerows. |
|  | Tafarn Newydd Children & Families Services (2) | 880 NE | Low | As above |
|  | Griffithstown Primary School (3) | 715 W | Low | Relatively distal from the Site with a low frequency of winds from source to receptor. |
|  | Griffithstown Infant and Nursery School (4) | 845 NW | Low | There is a medium frequency of winds towards the receptor and it is remote from the Site |
| Childcare | Cyfeillion Bach Nursery (5) | 515 W | Low | Relatively distal from the Site with a low frequency of winds from source to receptor. |
| Elderly Housing | Rowan House Nursing Home (6) | 830 NW | Low | Not downwind of prevailing conditions and distal from the Site. |
|  | Panteg Nursing Home (7) | 610 W-SW | Low | Located upwind of the dominant wind direction and not in close proximity to the Site. |
| Recreational Areas | Playing Field (8) | 200 N-NE | Medium | Downwind of prevailing conditions and reasonably close to source. |
|  | Craig-y-Felin Wood (9) | 340 S | Low | Although relatively proximal to the Site it is ocated upwind of the prevailing wind direction |
|  | Sports Ground (10) | 590 NW | Low | There is a medium frequency of winds towards the receptor and it is local to the Site |
|  | New Panteg Rugby & Football Club (11) | 602 N | Medium | Downwind of prevailing conditions and reasonably close to source. |
|  | Panteg Cricket Club (12) | 680 W-SW | Low | Located upwind of the Site and is reasonably distal. |
|  | Panteg Park (13) | 990 W | Low | Remote from the Site and there is a low frequency of winds from source to receptor |
| Places of Worship | New Inn Congregational Church (14) | 245 NE | Medium | Directly downwind of the Site and prevailing wind. Relatively proximal to the Site |
|  | St Marks Church Panteg (15) | 585 NE | Low | Although located downwind of the dominant prevailing wind it is considered relatively distal from the Site. Pathways are also restricted by intervening infrastructures, trees and hedgerows. |
|  | Griffithstown Baptist Church (16) | 715 NW | Low | Not downwind of prevailing conditions and distal from the Site. |
|  | Methodist Church (17) | 590 NE | Low | Directly downwind of the Site and prevailing wind but relatively distal from the Site |
|  | St Oswald Church in Wales (18) | 720 SW | Low | Located upwind of the dominant wind direction and not in close proximity to the Site. |
|  | Griffithstown Congregational Church (19) | 823 NW | Low | Not downwind of prevailing conditions and distal from the Site. |
|  | St Hildas Church Hall (20) | 910 NW | Low | As above |
|  | St Marys Church, Panteg Church Hall (21) | 890 N | Low | There is a high frequency of winds from source to receptor but the receptor is considered to be remote from the source |
| Other | Gwent Police (22) | 505 NE | Low | Directly downwind of the Site and prevailing wind but relatively distal from the Site |
|  | Railway Museum (23) | 527 W | Low | Relatively distal from the Site with a low frequency of winds from source to receptor. |
|  | Fire Station (24) | 670 NW | Low | Not downwind of prevailing conditions and distal from the Site. |
|  | New Inn Community Hall (25) | 730 N-NE | Low | Directly downwind of the Site and prevailing wind but relatively distal from the Site |
|  | Pontefelin Industrial Estate (26) | 0 – 576 N-NW | Medium | Although there is a low frequency of winds towards this receptor, it is adjacent to the Site |

Figure 1.  Sensitive Receptors within a 1km radius of the Site (red line denotes the boundary of the Site)

- Table 2   Distances to Selected, Representative Residential Properties/ Sensitive Locations (reference point refers to location numbered on figure 3).

| Location in relation to the Site | Reference Point | Min/Max Distance(m) from Site Boundary | Overall Exposure Levels |
| --- | --- | --- | --- |
| NE | Residential Housing Estate around Pont-y-felin Lane & Coed-y-felin, Lower New Inn (1) | 60-470 | Medium |
| NE | Residential Housing Estate around the Highway (2) | 405-1000 | Low |
| W | Residential Housing Estate adjacent to the railway track (3) | 320-1000 | Low |
| SE | Ty-Coch Farm (4) | 405 | Low |
| E-NE | Church Farm (5) | 705 | Low |
| SE | Ty-Cadno Farm (6) | 720 | Low |

- Figure 2. Residential Sensitive Receptors within a 1km radius of the Site (red line denotes the Site boundary)

fire prevention

Waste Storage Duration

The waste transfer station enclosure has a design capacity capable of separating up to 100 tonnes/day per day of incoming material. The maximum period of storage is 1 week with a further week for processing and/or removal of waste off Site. The short turn-around time of a maximum of 2 weeks ensures the mitigation against the build-up of hot spots.

    - Incoming wastes are typically processed on a first in first out basis, albeit that any potentially flammable wastes or wastes that have been placed in quarantined storage will be prioritised for removal.

The use of first in first out principles ensures the Site operates a rapid turnover of waste materials and that the waste transfer station bays are emptied every month so that all materials are removed and the bays are totally emptied (including the corners of the bay). This prevents the potential for any build-up of material and ensures that any degradable materials are rapidly removed.

Site cleaning procedures include sweeping out the bays and skips, including the corners, to ensure all material is removed and potentially combustible residues do not remain in-situ. Operational staff record the housekeeping of the bays and skips on the appropriate checklist, maintained in the Site office, ensuring the maximum emptying and cleaning frequency of 1 month is adhered to.

Waste streams are separated upon arrival ensuring incompatible wastes are stored and treated separately. All waste metals and vehicles are stored in adjacent bays constructed from fire-resistant concrete Legato L8 blocks which are located 16m from the waste transfer station enclosure containing incompatible household, commercial and industrial wastes.

Material contained within the waste transfer station enclosure are separated manually or by dedicated plant no longer than 1 day from deposit to ensure incompatible wastes are segregated from one another and any unstable wastes are stored appropriately either within a dedicated container for batteries or the quarantine area. Wastes are then transferred to the relevant bay on-Site according to the waste type.

    - All metal wastes, including ELV`s will be stored for no longer than one month. Any treatment or process carried out on such wastes will take place within this one-month interval. Household, commercial and industrial waste streams therefore remain on-Site for a shorter timeframe than metal wastes, ELV`s and wood. Table 3 below indicates the storage times of the waste streams accepted at the Site along with the duration on-Site for both the processed and un-processed material.

- Table 3    Storage Duration of Different Waste Streams

| Waste Type | Storage Duration |  |
| --- | --- | --- |
|  | Un-Processed | Processed |
| General Mixed Waste | 1 Week | 1 Week |
| Cardboard | 1 Week | 1 Week |
| Wood | 1 Week | 3 Weeks |
| Metal | 1 Week | 3 Weeks |
| ELV`s | 1 Week | 3 Weeks |

In the event of shutdown, waste will be diverted to alternative sites in the area. The preferred site is SL Recycling`s sister facility in Hengoed, which has the benefit of a Bespoke Environmental Permit.

Waste acceptance procedures require that unloading of waste deliveries are supervised by Site staff. The operational procedure involving clear out of bays and where necessary export of waste of up to a maximum of 100 t/day ensures short duration time and mitigation against heat build-up.

Quarantine area

A quarantine area is designated on the yard at a size of 8m x 8m with a height of 3m. It is clearly identified on Site and marked to allow the segregation of identified unsuitable material and separation from incoming waste. Quarantined waste is removed within 24 hours of deposit via the appropriate plant machinery on-Site (360° material handler, loader) depending on the waste type and size. It will be transported to an authorised facility that accepts the waste type quarantined in one of SL Recycling `s large goods vehicle (LGV) or heavy goods vehicle (HGV) as appropriate. Material subjected to a fire incident will be removed as soon as possible allowing for a suitably permitted site to be located (depending upon what the waste is and how its classified in accordance with WM3).

Suitable on-Site plant i.e. 360° material handler, loader or trucks will be used to transfer any material on-Site that needs to be transferred to the quarantine area such as burnt material or non-conforming waste types that have been inadvertently accepted or detected.

The quarantine area is in accordance with the Fire Prevention Plan Guidance in that it is clearly labelled, it has the capacity to hold at least 50% of the largest pile and it has a separation distance (from Site perimeter and other stored waste) of at least 6 metres around the quarantined waste. There is an adequate hose reel capacity to reach the quarantine area from the water storage tank.

Monitoring of STOCKPILES AND WASTE BAYS

    - All deliveries of incoming material to the reception bays are supervised by operational staff. All stockpiles are subjected to testing by a temperature probe at the start and end of the shift with results recorded on a log which is retained in the Site office. Operatives also visually inspect the waste piles for any signs of heat build-up or hot spots. Staff are trained in such methods (refer to paragraph 8.1.1 for details).

    - Due to the quick turnaround of waste on-site, the probability of self-combustion is unlikely, the most probable cause of fire is arson. The presence of the CCTV will therefore act as a deterrent and minimise the likelihood of a fire occurring.

    - In view of the fire prevention measures outlined above, the possibility of the fire spreading within the Site itself or to neighbouring locations is minimised.

All waste stockpiles in the waste transfer station enclosure, skips and external areas are inspected at the beginning and end of the operational day to identify any hot spots. A temperature probe used to detect the temperature of every stockpile during these inspections with a trigger level of 47°C used as an indicator of a hot spot. The piles are also turned either manually or with plant as appropriate on the last inspection of the day or more frequently in hot conditions (refer to paragraph 4.4.5).

Staff are trained to look for indicators of hot spots such as steam, smoke, flames or odours associated with heat (i.e. burning and smoke) during the inspections. In addition, inspections include the observation for the presence of dust, fluff and/or loose combustible material. Should any be found, housekeeping equipment in the form of brushes, shovels, mops and cleaning products will be used to remove the material prior to disposal in the appropriate container or bin.

During periods of hot weather (TCM to determine the level of heat defined as ‘hot weather’), all of the stockpiles on-Site are manually turned twice daily to allow for the even distribution of temperature and to enable any heat to dissipate.

The Environment Agency commissioned BRE Global Limited to carry out a review of Fire Prevention Plan document 160527 FPP v3 final draft. The BRE Global report includes the results of isothermal self-heating test data (based on test methodology in BS EN 15188 ‘’Determination of spontaneous ignition behaviour of dust accumulations’) on a range of waste types comprising: wood chip, rubber crumb and secondary recovered fuel (SRF). The time to ignition determined during the testing ranged from 74 to 106 days storage for a 4 m high stockpile of waste.

Waste stockpile heights on Site are a maximum of 4m, the height limit stipulated in the BRE Global review, and as waste stored in the bays and skips, including wood, paper, plastic etc are only stored on Site for a minimum of 2 weeks and a maximum of 1 month depending on waste types (refer to Table 1 for storage durations) it is highly unlikely that spontaneous ignition of waste will occur on site.  Notwithstanding this as a worst-case scenario, a trigger level of 47°C is used on site. This gives the Operator an early warning that temperatures may approach 57°C, which is the lowest critical temperature determined during the BRE Global trials for spontaneous ignition to occur in a 4m high stockpile of wood chip. This is seen as a very conservative approach to ensure that temperatures where spontaneous combustion could occur are never reached.

If the trigger level of 47°C is reached in any waste stockpile, the stockpile would be separated out, reduced in height, and doused with cold water throughout to reduce its temperature. Water would be applied via one of the three bowsers on-Site or by a hose and care taken to ensure that all materials are cooled by monitoring the temperature once hosing has ceased. This activity will be undertaken in the quarantine area and NRW will be informed.

Wastes are not burnt at the site and there is no waste incinerator plant on site therefore no source of ignition. Any hot works activities are undertaken in a designated bay bound on three sides by fire proofed walls and it is not conducted within 6m of any combustible or flammable waste.

Contingency Plans

In the event of an un-planned incident on Site, the waste delivery drivers will be contacted with instruction to divert their waste loads to an alternative permitted waste site (SL Recycling site in Hengoed).

Arson

The Site is surrounded by security fencing and lockable gates and controlled vehicular entry during working hours. The Site is also fitted with CCTV monitoring to detect any attempts at unauthorised entry.

LEAKS AND SPILLAGES

Oils and fuels stored on-Site from the depollution process and for maintenance purposes are stored in drums which are placed on drip trays to contain any leaks or spillages. They are inspected twice daily at the beginning and end of the working day for any defects or deterioration of the drums.

A registered facility collects or empty the drums when they are three-quarters full and transfer off-Site for disposal or recovery.

In order to prevent fuels and combustible liquids leaking or trailing from Site vehicles, they are inspected twice daily for any leaks. Spill kits are kept in all of the facilities trucks, vans and plant. In addition, there are spill kits in the ELV area and in strategic places around the Site. Reference should be made to drawing SLR_site_layout for their locations.

On receipt of ELV`s at the weighbridge, a Site operative inspects the vehicle for leaks or spillages to prevent any fuels or oils being dispersed around the Site. If a leak is identified, it will be contained whilst the vehicle is transported to the de-pollution area and, should there be any spillages, spill kits will be used to absorb the liquid. Once the ELV`s have been de-polluted, they are inspected again for any leaks.

The materials used for cleaning-up any spillages will be placed in the disposable bag provided in the spill kit and secured with the tie. The bag is then transferred to a relevant licenced facility which accepts such wastes.

Plant and Equipment

An Operating and Maintenance Manual is held by Site management in line with SL Recycling procedures for plant and equipment. As a part of these procedures all plant and equipment on Site which requires maintenance are assessed for fire risk. Checks are programmed and records retained with a log of maintenance carried out.

    - Site vehicles are fitted with dust filters and fire extinguishers. Vehicles and equipment are regularly inspected for electrical faults, tramp metal, dust, fluff and for any fuel or combustible liquid leakages. Spill kits are readily available on the Site and within each vehicle in the event of such leaks. When not in use mobile plant are stored away from any combustible waste materials. A log of inspection and maintenance of all plant and equipment will be maintained which will include a record of any spills/leakages and/or the presence of tramp metal and the action taken.

Electrical Faults

All electrical work on Site is carried out by fully certified qualified electricians and it complies with the relevant British Standard for design and installation of electrical equipment. Detailed operational manuals for any equipment requires equipment to be checked and maintained as part of a planned maintenance regime. Vehicles and equipment are inspected daily by Site operators for electrical faults and serviced as required for each specific type of equipment or plant

Smoking Policy

The Site operates a strict no smoking policy.

Hot Works

For the purposes of burning off alloy wheels and for cutting oversize metal prior to processing, a hot works `burning  bay` is installed on the Site.

A hot work management system is operated and applies to staff and contractors. A fire watch is carried out after hot works are finished and specifically revisited at the end of the working day by staff trained in the assessment of risks associated with hot work.

All hot works is carried out by trained personnel and is restricted to the designated Hot Works Bay surrounded on three sides by a fire wall constructed of Legato LG8 blocks.

Industrial Heaters

There are no industrial heaters installed at the facility.

Fire Watch

At the beginning and end of each working shift a Fire Watch is carried out by suitably trained staff. In addition to CCTV, temperature probes and visual inspections to detect any evidence of fire or hot spots is carried out. Results are recorded on the housekeeping and inspection log and assessed to see if any improved operational procedures can be invoked to reduce risks. Fire watch reviews are also undertaken out of hours to check for post operational heating issues and procedures are reviewed after assessment.

All waste storage areas and the external yard area on Site are subject to the Fire Watch checks. Inspections, carried out at a minimum of 10 minutes after plant, machinery and vehicles have been switched off, also check for dust build up or fluff settled onto hot exhausts and engines on plant. Should there be any dust, fluff or debris deposited at any location across the yard, it will be removed via the use of housekeeping equipment such as brushes, cloths, sponges and cleaning products where appropriate and transferred to a dedicated bin, container or the quarantine area as applicable.

management and storage of waste

Waste Acceptance Procedures

Detailed waste acceptance procedures are noted within the EMS for site.

The facility benefits from the integration of the FRED software system in the weighbridge office which enables the monitoring of the weights of waste feedstock to ensure the Site does not exceed the amounts stipulated in the permit.

In view of the nature of the waste streams accepted at the Site, it is not anticipated that there will be seasonal variations in demand or supply. As a consequence of ‘zero landfill’ and the avoidance to dispose of waste to landfills coupled with the promotion of re-use and recycle, the need for recycling facilities such as SL Recycling has increased of late, and it is considered that the resilience of the supply chain and end users is viable in foreseeable market conditions.

A visual inspection of the contents of all waste loads, including those received in enclosed skips, are made during deposit.

Any discrepancies found resultant from the checks detailed results in the vehicle being detained whilst some, or all, of the following supplementary management decisions are taken:

      - Referral to a Technically Competent Person (TCP) on site;

      - Referral to the waste producer to confirm the nature of the waste load;

      - Referral to the waste carrier’s base;

      - Referral to National Resources Wales;

      - Redirection of delivery vehicle off Site, to a suitably authorised facility; and

      - If the waste has been discharged on the floor of the building or external storage area, removal of the waste to the secure quarantine area, prior to off-Site removal either to the waste producer or suitably authorised facility.

Any wastes discovered to be a hot load or have the potential to be a hot load are identified and removed from the Site as a matter of urgency, or temporarily stored in the designated quarantine area.

    - In the quarantine area, wastes are kept segregated from other wastes which are or are likely to be incompatible. Quarantined wastes (including any inadvertently received powdery or excessively dusty wastes) are stored in a sealed and lidded container and removed from the Site as a priority incident and within 24 hours, subject to an authorised facility being able to accept them within this timescale. Such wastes will be dampened down (if required) using a hose prior to being transferred to quarantine or handling in any way so that dust emissions during handling are minimised.

Wastes are not accepted if for any reason there is insufficient storage capacity available or if the Site is inadequately manned. This is to ensure that all waste is managed effectively to prevent pollution or loss of amenity.

All separation distances between waste stockpile & buildings, where relevant, are shown on drawing SLR_site_layout.

Identification of Potential Sources of Fire

In constructing robust risk-based management protocols for the Site, it is recognised that there are a number of potential sources of fire associated with the waste transfer station, wood storage and treatment and scrap metal, vehicle storage, depollution and dismantling facility from:

      - Vehicles and plant delivering and processing wastes to/at the facility; and

      - Waste storage, bulking up, storage and dispatch.

These matters are addressed further in the relevant sections below.

Waste Feedstock Inventory and Source Materials

With due regard to the potential for waste feedstock material to be an inherent fire risk, key waste streams received at the facility are detailed in Appendix 1. Assessment of the associated fire potential under ‘normal’ operational conditions is provided.

Waste Transfer Station ENCLOSURE

The waste transfer station enclosure comprises of walls to either side constructed of Legato L8 blocks and a canopy roof for processing general waste. The maximum storage is two weeks which also includes the processing time. For mixed material brought to the Site there is the capability for up to 50 tonnes/day to be processed with up to 50 tonnes/day to be disposed as waste at an appropriate authorised site.

At a conversion rate of 650kg/m3 residual waste (WRAP) this equates to a pile size requirement of up to 250m3 each. These figures are well within the Guidance figures for maximum pile size for relevant wastes.

The walls of the enclosure are 4m high and all material stored inside do not exceed this height therefore giving a freeboard of 1m to the top of the canopy. The enclosure is isolated from other stockpiles on-Site with the closest being the wood storage bay at 12m to the north.

Scrap Metal, Vehicle Storage, Depollution and Dismantling Area

External bays are used for scrap metal storage, treatment, vehicle dismantling and depollution, depolluted car storage and wood storage. Bay walls comprise fireproof LG8 Legato blocks.

All externally stored wastes, including the unpolluted cars, depollution and dismantling area, wood storage area and scrap metal storage area comprises impermeable pavement with sealed drainage system to petrol/oil interceptor.

Lead acid batteries, e.g. removed from cars during depollution, are stored in a skip with an acid resistant base and cover to prevent ingress of rainwater.

Metal filings and turnings are stored in a separate enclosed skip with impermeable base and cover to prevent ingress of rainwater.

Vehicle dismantling and depollution activities involves:

The End of Life Vehicles are received via the weighbridge, where they are inspected for quality and contamination prior to transferal to designated depollution bays within the Site.

These bays are fitted with interceptor drainage systems to eliminate the possibility of ground contamination. The motor vehicles are manually depolluted. Batteries, if present, are removed first as a part of on-Site procedures.

Metal recycling involves the sorting, separation, grading, shredding, shearing, compacting, granulating of cables and cutting (using only hand-held equipment) of ferrous metals or alloys and non-ferrous metals for recovery. Storage and recovery of waste motor vehicles also take place on Site in a designated bay with treatment comprising of dismantling and depollution only.

    - Metal wastes and ELV`s remain on-Site for no longer than one month which includes storage, processing and treatment as specified above. The height of the storage bays are 4 m and stockpiles do not exceed 3 m. A line 1 m below the top of the bay walls is marked clearly to ensure stockpile heights do not exceed 3 m. To prevent any fires overlapping the side walls of the bay into adjacent waste stacks, a line clearly painted inside the bay along the floor is positioned 1m from the front to ensure waste piles are not stored beyond this line.

    - The waste bays are separated by fireproof walls constructed with `Legato LG8 blocks. These pertain to A1 fire-resistant classification in accordance with REI 240 standards rendering the Legato blocks fire-resistant for up to at least 4 hours. They have been installed in accordance with the manufacturer’s recommendations.

Wood Waste for recovery

Waste wood storage, sorting and separation activities involves:

The wood waste material are received via the weighbridge, where it is inspected for quality and contamination prior to transferal to the designated external secured bay within the Site adjacent to the metal recycling bays.

These bays are fitted with impermeable pavement with sealed drainage system to petrol/oil interceptor to eliminate the possibility of ground contamination and the bay walls comprise of LG8 Legato fireproof blocks

The maximum storage of waste is one month with sorting and separation taking place within the first seven days. With the dimensions 10 m x 10 m, the bays have the capability for up to 50 tonnes/day to be processed with up to 50 tonnes/day to be disposed as waste at an appropriate authorised site.

Waste delivery vehicles are directed to reverse into the wood waste bay where waste loads are tipped onto the floor and bulked up within the confines of the bay wall constructed with Legato LG8 blocks using a loading shovel or similar by a suitably trained Site operative. Wastes are stored in the bay prior to sorting and separation into different components for recovery or disposal at an authorised site as appropriate.

    - The height of the storage bays are 4 m and stockpiles do not exceed 3 m. A line 1 m below the top of the bay walls is marked clearly to ensure stockpile heights do not exceed 3 m in order to prevent fire spreading over the walls. This also ensures no wastes within the stockpiles exceed the height of the bay walls thus avoids bridging. A line is also clearly marked on the floor across the length of each bay at 1m distance from the front wall to enable any flames or fires spreading to adjacent bays. The waste bays are separated by fireproof walls constructed with Legato LG8 blocks. These pertain to A1 fire-resistant classification in accordance with REI 240 standards rendering the Legato blocks fire-resistant for up to at least 4 hours.

    - Table 4 provides details of stockpile sizes, storage bay and container dimensions. The stockpile ID numbers denote the location of the stockpile on the Site plan, reference SLR_site_layout.

- Table 4 Stockpile and Storage Dimensions

| Stockpile ID | Maximum Stockpile Dimensions (L x W x H) | Waste volume (m3) | Bay/Storage Area Dimensions | Approximate tonnage |
| --- | --- | --- | --- | --- |
| 1.Skip for batteries | 1.8m x 1.3m x 0.9m | 2.106 | 1.8m x 1.3m x 0.9m | 3 |
| 2.Metal Processing Pile | 10m x 9m x 3m | 270 | 10m x 10m x 4m | 115 |
| 3.Metal Storage Bays | 10m x 9m x 3m | 270 | 10m x 10m x 4m | 115 |
| 4.Hot Works Bay | 10m x 9m x 3m | 270 | 10m x 10m x 4m | 115 |
| 5.Vehicle Depollution Bay | 15m x 5m x 3m | 225 | 24m x 10m x 4m |  |
| 6.Wood Storage and Treatment Bay | 10m x 9m x 3m | 270 | 10m x 10m x 4m | 100 |
| 7.Waste Transfer Station Building | 12m x 8m x 4m | 384 | 12m x 8m x 5m | 100 |
| 8.Cardboard | 10m x 5m x 3m | 120 | 10m x 5m x 12m | 25 |

FIRE DETECTION and Fire Fighting

Fire Detection

Waste materials stored throughout the Site are routinely inspected at regular intervals as detailed above. They are all visually inspected, and the temperature is measured via an accredited temperature probe.

Any evidence of a hot spots triggers an assessment of the most appropriate action which may be the pulling apart of the stack to dissipate heat by the on-Site material handler, the transferal of material to the quarantine area or the application of cooling water.

Portable fire extinguishers are available at the Site and staff are trained in their use. Records of training testing and maintenance of fire extinguishers are kept in the Site`s office. Fire extinguishers meet the requirements of BS 5036.

provision and management of firewater

A firewater storage tank connected to the local water supply is provided and designed in accordance with the requirements of BS5306. The water supply feed and tank is insulated to prevent cold weather freezing. The capacity of the water storage tank is a minimum of 300m3. There are also three water bowsers on-Site with a capacity of 1.125 m3 that are refilled after use as a Site procedure and checked daily during inspections to ensure they contain water at the combined maximum capacity of 3.375 m3 at all times.

At maximum pile size of 384m3 based on the largest stockpile in the waste transfer station enclosure with the dimensions of 12m x 8m and a height of 4m and, applying the Guidance rate of 2m3 /min water for a minimum of 3hrs for a 384m3 pile of waste would require 460.8m3 of water. An on-Site water storage tank with a volume of 300 m3 would be supplemented by water from the on-Site lagoon which has a perimeter of 77.4m and the capacity to store 410m3 of water.

Combined with the other sources available, this is adequate for the waste piles on site. Given that the lagoon is located in a portion of the Site that is designated as a Flood Zone 2, the lagoon is at full capacity for the majority of the year, therefore it is considered to be a reliable source of water. During dry conditions, the lagoon will be manually topped-up from the on-Site hydrant to ensure there is a constant and adequate supply of firewater.

The Operator is in the process of procuring a fire engine for the Site in order to enhance the firefighting potential at the facility. Details will be included into the FPMP once confirmed.

There is additionally a fire hydrant adjacent to the quarantine area and proximal to the entrance to the Site. This is shown on Drawing SLR_site_layout. The utilisation of this fire hydrant has been confirmed by Blackwood Fire, a specialist fire protection service and by the South Wales Fire and Rescue Service. It is important to note that the Fire Service are no longer permitted to test the flow rates of fire hydrants due to the discolouration it causes and the potential to taint water supplies. As such, the exact details regarding the flow rate of the hydrant is unavailable although typically, the average flow rate of fire hydrants in the UK is 8 litres/sec equating to 28m3/min or 86m3 over the course of 3 hours.

The total water capacity stored on-Site amounts to 713.375m3 in total from the water tank and lagoon which would provide sufficient water for in excess of 3 hours for a 384m3 pile. Including the fire hydrant and based on its use for 3 hours, there is 799.375m3 of water available. It is considered that the fire service would be able to attend an incident in significantly less time than 3 hours (the closest Fire Station is located c.2.5m north of the Site) and that upon arrival there would be a readily accessible supply of water available for use from the on-Site fire hydrant the Site drainage lagoon, recirculated firefighting waters and (if appropriate/required) the adjacent Afon Lywd.

All surface run-off from the external yard area currently discharges via an interceptor to the on-Site lagoon. To assist in the containment of fire water and to prevent it discharging to sewer, drainage mats will be installed in the drains on-site as well as those immediately adjacent to the perimeter. These are stored in the office and in the pre-existing building. Firewater would then be potentially available for reuse by the fire service or would be removed by tanker and transferred to an appropriately licensed wastewater treatment facility.

In the event that storage of firefighting water was required on Site, the impermeable bunded area at the rear of the Site with drain mats blocking the run-off creates a storage area of 125m x 80 m x min 0.1m depth giving a capacity to retain up to 1000m3 which is in excess of the amount required to extinguish the worst-case fire, that being a 384m3 stockpile requiring 460.8m3 of fire water. This could be stored prior to controlled release into the lagoon for further firefighting or for appropriate controlled removal from the Site.

The waste transfer station enclosure has a watertight floor and the enclosure is surrounded by a kerbed area which directs retained firewater into the Site drainage system. Fire-fighting water in the enclosure overflows onto the yard which is kerbed. When the kerbed area has filled, this area overflows and, by gravity, drains from the building into the Site surface drainage system to a lagoon, via the interceptor. Firewater is then potentially available for reuse by the fire service or removed by tanker and transferred to an appropriately licensed wastewater treatment facility.

The wood storage pile is surrounded by Legato LG8 fireproof retaining walls to the rear and the sides. Fire water in this area is retained by kerbing which when full overflows to the Site drainage system draining to the lagoon.

The vehicle dismantling and de-pollution area is surrounded by a kerbed area and Legato LG8 fire walls which separate it from the wood storage area and the metal storage and processing area. Fire water in this area also overflows to the Site drainage system draining to the lagoon.

The metal storage and processing area is surrounded by Legato LG8 firewalls and kerbed area separating it from the external boundary, the vehicle dismantling area and hot work bay area. Fire water in this section overflows to the Site drainage system draining to the lagoon.

The Hot Works Bay is surrounded to the rear and sides by firewalls constructed with Legato LG8 blocks. Firewater drains to the site drainage system and pass to the lagoon storage. The entire surface of the Site is concreted therefore there are no permeable areas for the ingress of firewater.

Fire INCIDENT ProcedurE-emergency plan

Staff operatives who will be engaging in firefighting activities and those who operate the plant complete a Fire Marshall training course conducted by a third-party safety management company, XYZ Training Group who are affiliated with the National Training Card Scheme.

Plant that would be utilised in the event of a fire are all fitted out with fire and heat protected hydraulic systems, fire extinguishers and an enclosed cab. Those to be deployed are as follows:

A front end loader;

A dump truck;

A fire engine (to be purchased soon);

A 360° material handler; and,

Water Bowsers x 3

The Sites internal access road is designed as a one-way system and provides straightforward and rapid access to all areas of the Site for the plant that will be designated to assist in fire-fighting or fire prevention.

Should there be any unburnt material in or adjacent to the fire, plant machinery will be used to separate and load into the truck for transferal to a safe section of the site. Operators on-Site who have trained as Fire Marshalls will douse any unburned stockpiles, material or hazards in the vicinity of the fire with water supplied from one of the water bowsers or the hose pipe to prevent the fire from spreading.

Emergency procedures for the Site has been developed and is the subject of training and exercising for all staff engaged at the Site. The Plan sets out the following key points:

Fire actions and reporting procedures;

Emergency Procedures including communication and evacuation;

Identification of off-Site fire assembly point;

Circumstances under which trained staff may be involved in actions to separate affected waste;

Diversion of incoming materials to their own sister site or one of the two nearest waste facilities located 665m to the north (Biffa) and 151m to the south-east of the Site (Recycled Solutions);

Recovery including appropriate removal of burned waste to an authorised facility and the tankering of any residual firewater by a licensed waste transfer operator to an appropriately permitted wastewater treatment facility;

Should the plant and machinery on-Site prove to be insufficient for the removal of burnt waste, additional plant will be sourced from the Operators sister site in Hengoed;

A copy of the Fire Emergency Plan is retained at the Site office.

Key actions to be undertaken in the event of discovering a fire are detailed in Table 3 below. Key Actions on discovering a fire

Box 1 - Action on discovering a fire

- Fire service to be informed immediately of the location of the fire and the waste types involved; - All personnel must follow Emergency Fire Plan; - Neighbouring businesses, residents and sensitive receptors will be informed via telephone (note that there is a contact list held in the Site office that is updated regularly); - Fire extinguishers and water hoses must only be used by trained fire marshals and when it is safe and appropriate to do so - Once the Site is cleared of burnt material and firewater, the yard area will be washed down before replacing or repairing damaged equipment and/or infrastructure as necessary. - Electrical checks and the re-evaluation of contingency plans will also be carried out prior to the Site becoming operational again.

Reviewing and Monitoring the FPMP

Reviewing

This FPMP is a live working document which is reviewed quarterly or more frequently to reflect any changes to the facility such as the acceptance of additional waste streams (specifically those that are combustible), the modification of infrastructure, the inclusion of additional infrastructure or buildings, the installation of additional plant, machinery or equipment, following a fire incident and/or increasing or decreasing waste volumes.

All staff are made aware of the contents and the location of this FPMP during inductions and following a review. It is kept in the Site office and is accessible to all staff, visitors and contractors.

Training, MONITORING and Site Inspections

All Site supervisors, of which at least one will be on Site at any one time, will undertake a Fire Safety Training course for Fire Marshalls with XYZ Training Group who are affiliated with the National Training Card Scheme.

Fire Marshalls will induct new starters and conduct quarterly refresher courses for all staff to include on-Site drills and exercises. This is to ensure all staff are competent to carry out the measures and procedures outlined within this FPMP.

Records of training, exercise drills and refresher course will be kept in a designated folder and maintained in the office on-Site.

Site inspections are carried out at the start and the end of the working day. This will include the visual inspection of all the stockpiles for hot spots and the recording of the temperatures on the appropriate logging sheet which is retained in the Site office. This allows for the identification of any signs or patterns of a constant temperature increase in a particular waste stack.

During the Site inspections, all equipment and plant are checked to ensure they are either operating or turned off correctly and that there are no identifiable ignition sources. All plant, equipment and fire prevention and mitigation equipment are maintained and serviced as per manufacturers recommendations and by qualified personnel as appropriate. Records of all inspections and servicing are maintained in a designated folder which is kept in the Site office.

- APPENDIX 1	 WASTE FEEDSTOCK INVENTORY AND SOURCE MATERIALS

| Waste Code | Description | Fire Risk |
| --- | --- | --- |
| 01 | Waste resulting from exploration, mining, quarrying and physical and chemical treatment of minerals |  |
| 01 01 | Wastes from mineral excavation |  |
| 01 01 01 | wastes from mineral metalliferous excavation | Low |
| 01 01 02 | wastes from mineral non-metalliferous excavation | Low |
| 01 03 | wastes from physical and chemical processing of metalliferous minerals |  |
| 01 03 06 | tailings other than those mentioned in 01 03 04 and 01 03 05 | Low |
| 01 03 09 | red mud from alumina production other than the wastes mentioned in 01 03 07 | Low |
| 01 04 | wastes from physical and chemical processing of non-metalliferous minerals |  |
| 01 04 08 | waste gravel and crushed rocks other than those mentioned in 01 04 07 | Low |
| 01 04 09 | waste sand and clays | Low |
| 01 04 11 | wastes from potash and rock salt processing other than those mentioned in 01 04 07 | Low |
| 01 04 12 | tailings and other wastes from washing and cleaning of minerals other than those mentioned in 01 04 07 and 01 04 11 | Low |
| 01 04 13 | wastes from stone cutting and sawing other than those mentioned in 01 04 07 02 WASTES FROM AGRICULTURE, HORTICULTURE, AQUACULTURE, FORESTRY | Low |
| 02 | Wastes from agriculture, horticulture, aquaculture, forestry, hunting and fishing, food preparation and processing |  |
| 02 01 | Wastes from agriculture, horticulture, aquaculture, forestry, hunting and fishing |  |
| 02 01 03 | plant-tissue waste | Med |
| 02 01 04 | waste plastics (except packaging) | Med |
| 02 01 07 | wastes from forestry | Med |
| 02 01 10 | waste metal | Low |
| 02 02 | wastes from the preparation and processing of meat, fish and other foods of animal origin |  |
| 02 02 03 | materials unsuitable for consumption or processing | Low |
| 02 03 | wastes from fruit, vegetables, cereals, edible oils, cocoa, coffee, tea and tobacco preparation and processing; conserve production; yeast and yeast extract production, molasses preparation and fermentation |  |
| 02 03 04 | materials unsuitable for consumption or processing | Low |
| 02 04 | wastes from sugar processing |  |
| 02 04 01 | soil from cleaning and washing beet | Low |
| 02 04 02 | off-specification calcium carbonate | Low |
| 02 05 | wastes from the dairy products industry |  |
| 02 05 01 | materials unsuitable for consumption or processing | Low |
| 02 06 | wastes from the baking and confectionery industry |  |
| 02 06 01 | materials unsuitable for consumption or processing | Low |
| 02 06 02 | wastes from preserving agents | Low |
| 02 07 | wastes from the production of alcoholic and non-alcoholic beverages (except coffee, tea and cocoa |  |
| 02 07 01 | wastes from washing, cleaning and mechanical reduction of raw materials | Low |
| 02 07 02 | wastes from spirits distillation | Med |
| 02 07 04 | materials unsuitable for consumption or processing | Med |
| 03 | Wastes from wood processing and the production of panels and furniture, pulp, paper and cardboard |  |
| 03 01 | Wastes from wood processing and the production of panels and furniture |  |
| 03 01 01 | Waste bark and cork | Med |
| 03 01 05 | sawdust, shavings, cuttings, wood, particle board and veneer other than those mentioned in 03 01 04 | Med |
| 03 03 | Wastes from pulp, paper and cardboard production and processing |  |
| 03 03 01 | Waste bark and wood | Med |
| 03 03 07 | mechanically separated rejects from pulping of waste paper and cardboard | Med |
| 03 03 08 | wastes from sorting of paper and cardboard destined for recycling | Med |
| 03 03 10 | Fibre rejects, fibre-, filler- and coating-sludges from mechanical separation | Med |
| 04 | Wastes from the leather, fur and textile industries |  |
| 04 01 | Wastes from the leather and fur industry |  |
| 04 01 08 | waste tanned leather (blue sheetings, shavings, cuttings, buffing dust) containing chromium | Med |
| 04 01 09 | wastes from dressing and finishing | Med |
| 04 02 | wastes from the textile industry |  |
| 04 02 21 | wastes from unprocessed textile fibres | Med |
| 04 02 22 | wastes from processed textile fibres | Med |
| 06 | Wastes from inorganic chemical processes |  |
| 06 09 | wastes from the MSFU of phosphorous chemicals and phosphorous chemical processes |  |
| 06 09 02 | Phosphorous slag | Med |
| 06 09 04 | calcium-based reaction wastes other than those mentioned in 06 09 03 | Low |
| 06 11 | wastes from the manufacture of inorganic pigments and opacificiers |  |
| 06 11 01 | calcium-based reaction wastes from titanium dioxide production | Low |
| 07 | Wastes from organic chemical processes |  |
| 07 02 | wastes from the MFSU of plastics, synthetic rubber and man-made fibres |  |
| 07 02 13 | Waste plastic | Med |
| 09 | Wastes from the photographic industry |  |
| 09 01 | Wastes from the photographic industry |  |
| 09 01 07 | photographic film and paper containing silver or silver compounds | Med |
| 09 01 08 | photographic film and paper free of silver or silver compounds | Med |
| 09 01 10 | single-use cameras without batteries | Med |
| 09 01 12 | single-use cameras containing batteries other than those mentioned in 09 01 11 | Med |
| 10 | Wastes from thermal processes |  |
| 10 01 | Wastes from power stations and other combustion plants |  |
| 10 01 01 | Bottom ash and slag only | Low |
| 10 01 05 | Gypsum (solid) only | Low |
| 10 01 07 | calcium-based reaction wastes from flue-gas desulphurisation in sludge form | Low |
| 10 01 15 | Bottom ash and slag only from co-incineration other than those mentioned in 10 01 14 | Low |
| 10 01 19 | wastes from gas cleaning other than those mentioned in 10 01 05, 10 01 07 and 10 01 18 | Low |
| 10 01 24 | sands from fluidised beds | Low |
| 10 02 | Wastes from the iron and steel industry |  |
| 10 02 01 | Wastes from the processing of slag | Low |
| 10 02 02 | Unprocessed slag | Low |
| 10 02 08 | Solid wastes from gas treatment other than those mentioned in 10 02 07 | Low |
| 10 02 10 | Mill scales | Low |
| 10 02 14 | Filter cakes from gas treatment other than those mentioned in 10 02 13 | Low |
| 10 02 15 | Other filter cakes | Low |
| 10 03 | Wastes from aluminium thermal metallurgy |  |
| 10 03 02 | Anode scraps | Med |
| 10 03 05 | Waste alumina | Med |
| 10 03 16 | Skimmings other than those mentioned in 10 03 15 | Med |
| 10 03 18 | Carbon-containing wastes from anode manufacture other than those mentioned in 10 03 17 | Low |
| 10 03 24 | Solid wastes from gas treatment other than those mentioned in 10 03 23 | Low |
| 10 03 26 | Filter cakes from gas treatment other than those mentioned in 10 03 25 | Low |
| 10 03 28 | Wastes from cooling-water treatment other than those mentioned in 10 03 27 | Low |
| 10 03 30 | Wastes from treatment of salt slags and black drosses other than those mentioned in 10 03 29 | Low |
| 10 04 | Wastes from lead thermal metallurgy |  |
| 10 04 10 | Wastes from cooling-water treatment other than those mentioned in 10 04 09 | Low |
| 10 05 | Wastes from zinc thermal metallurgy |  |
| 10 05 01 | slags from primary and secondary production | Low |
| 10 05 09 | wastes from cooling-water treatment other than those mentioned in 10 05 08 | Low |
| 10 05 11 | dross and skimmings other than those mentioned in 10 05 10 | Low |
| 10 06 | wastes from copper thermal metallurgy |  |
| 10 06 01 | slags from primary and secondary production | Low |
| 10 06 02 | dross and skimmings from primary and secondary production | Low |
| 10 06 10 | wastes from cooling-water treatment other than those mentioned in 10 06 09 | Low |
| 10 07 | wastes from silver, gold and platinum thermal metallurgy |  |
| 10 07 01 | slags from primary and secondary production | Low |
| 10 07 02 | dross and skimmings from primary and secondary production | Low |
| 10 07 03 | solid wastes from gas treatment | Low |
| 10 07 05 | filter cakes from gas treatment | Low |
| 10 07 08 | wastes from cooling-water treatment other than those mentioned in 10 07 07 | Low |
| 10 08 | wastes from other non-ferrous thermal metallurgy |  |
| 10 08 09 | other slags | Low |
| 10 08 11 | dross and skimmings other than those mentioned in 10 08 10 | Low |
| 10 08 13 | carbon-containing wastes from anode manufacture other than those mentioned in 10 08 12 | Low |
| 10 08 14 | anode scrap | Low |
| 10 08 18 | filter cakes from flue-gas treatment other than those mentioned in 10 08 17 | Low |
| 10 08 20 | wastes from cooling-water treatment other than those mentioned in 10 08 19 | Low |
| 10 09 | wastes from casting of ferrous pieces |  |
| 10 09 03 | furnace slag | Low |
| 10 09 06 | casting cores and moulds which have not undergone pouring other than those mentioned in 10 09 05 | Low |
| 10 09 08 | casting cores and moulds which have undergone pouring other than those mentioned in 10 09 07 | Low |
| 10 09 14 | waste binders other than those mentioned in 10 09 13 | Low |
| 10 09 16 | waste crack-indicating agent other than those mentioned in 10 09 15 | Low |
| 10 10 | wastes from casting of non-ferrous pieces |  |
| 10 10 03 | furnace slag | Low |
| 10 10 06 | casting cores and moulds which have not undergone pouring other than those mentioned in 10 10 05 | Low |
| 10 10 08 | casting cores and moulds which have undergone pouring other than those mentioned in 10 10 07 | Low |
| 10 10 14 | waste binders other than those mentioned in 10 10 13 | Low |
| 10 10 16 | waste crack-indicating agent other than those mentioned in 10 10 15 | Low |
| 10 11 | Wastes from manufacture of glass and glass products |  |
| 10 11 03 | waste glass-based fibrous materials | Low |
| 10 11 10 | waste preparation mixture before thermal processing, other than those mentioned in 10 11 09 | Low |
| 10 11 12 | Clean glass other than those mentioned in 10 11 11 | Low |
| 10 11 16 | solid wastes from flue-gas treatment other than those mentioned in 10 11 15 | Low |
| 10 11 18 | filter cakes from flue-gas treatment other than those mentioned in 10 11 17 | Low |
| 10 12 | Wastes from manufacture of ceramic goods, bricks, tiles and construction products |  |
| 10 12 01 | waste preparation mixture before thermal processing | Low |
| 10 12 05 | filter cakes from gas treatment | Low |
| 10 12 06 | discarded moulds | Low |
| 10 12 08 | Waste ceramics, bricks, tiles and construction products (after thermal processing) | Low |
| 10 12 10 | solid wastes from gas treatment other than those mentioned in 10.12 09 | Low |
| 10 12 12 | wastes from glazing other than those mentioned in 10.12.11 | Low |
| 10 13 | Wastes from manufacture of cement, lime and plaster and articles and products made from them |  |
| 10 13 01 | waste preparation mixture before thermal processing | Low |
| 10 13 04 | wastes from calcination and hydration of lime | Low |
| 10 13 07 | filter cakes from gas treatment | Low |
| 10 13 10 | wastes from asbestos-cement manufacture other than those mentioned in 10 13 09 | Low |
| 10 13 11 | wastes from cement-based composite materials other than those mentioned in 10 13 09 and 10 13 10 | Low |
| 10 13 13 | solid wastes from gas treatment other than those mentioned in 10 13 12 | Low |
| 10 13 14 | Waste concrete only | Low |
| 11 | Wastes from chemical surface treatment and coating of metals and other materials; non-ferrous hydro metallurgy |  |
| 11 01 | Wastes from chemical surface treatment and coating of metals and other materials (for example galvanic processes, zinc coating processes, pickling processes, etching, phosphating, alkaline degreasing, anodising) |  |
| 11 01 10 | filter cakes other than those mentioned in 11 01 09 | Low |
| 11 01 14 | degreasing wastes other than those mentioned in 11 01 13 | Low |
| 11 02 | wastes from non-ferrous hydrometallurgical processes |  |
| 11 02 03 | wastes from the production of anodes for aqueous electrolytical processes | Low |
| 11 02 06 | wastes from copper hydrometallurgical processes other than those mentioned in 11 02 05 | Low |
| 11 05 | wastes from hot galvanising processes |  |
| 11 05 01 | hard zinc | Low |
| 11 05 02 | zinc ash | Low |
| 12 | Wastes from shaping and physical and mechanical surface treatment of metals and plastics |  |
| 12 01 | wastes from shaping and physical and mechanical surface treatment of metals and plastics |  |
| 12 01 01 | ferrous metal filings and turnings | Low |
| 12 01 03 | non-ferrous metal filings and turnings | Low |
| 12 01 05 | plastics shavings and turnings | Low |
| 12 01 13 | welding wastes | Low |
| 12 01 17 | waste blasting material other than those mentioned in 12 01 16 | Low |
| 12 01 21 | spent grinding bodies and grinding materials other than those mentioned in 12 01 20 | Low |
| 15 | Waste packaging |  |
| 15 01 | Packaging (including separately collected municipal packaging waste) |  |
| 15 01 01 | paper and cardboard packaging | Med |
| 15 01 02 | Plastic packaging | Med |
| 15 01 03 | Wooden packaging | Med |
| 15 01 04 | Metallic packaging | Low |
| 15 01 05 | Composite packaging | Low |
| 15 01 06 | Mixed packaging | Med |
| 15 01 07 | Glass packaging - Clean glass only | Low |
| 15 01 09 | Textile packaging | Med |
| 15 02 | absorbents, filter materials, wiping cloths and protective clothing |  |
| 15 02 03 | absorbents, filter materials, wiping cloths and protective clothing other than those mentioned in 15 02 02 | Med |
| 16 | Wastes not otherwise specified in the list |  |
| 16 01 | end-of-life vehicles from different means of transport [including off-road machinery] and wastes from dismantling of end-of-life vehicles and vehicle maintenance (except 13,14, 16 06 and 16 08) |  |
| 16 01 03 | end-of-life tyres | Med |
| 16 02 | wastes from electrical and electronic equipment |  |
| 16 02 14 | discarded equipment other than those mentioned in 16 02 09 to 16 02 13 | Low |
| 16 02 16 | components removed from discarded equipment other than those mentioned in 16 02 15 | Low |
| 16 03 | off-specification batches and unused products |  |
| 16 03 04 | inorganic wastes other than those mentioned in 16 03 03 | Low |
| 16 03 06 | organic wastes other than those mentioned in 16 03 05 | Low |
| 16 06 | batteries and accumulators |  |
| 16 06 04 | alkaline batteries (except 16 06 03) | Med |
| 16 06 05 | other batteries and accumulators | Med |
| 16 11 | waste linings and refractories |  |
| 16 11 02 | carbon-based linings and refractories from metallurgical processes others than those mentioned in 16 11 01 | Low |
| 16 11 04 | other linings and refractories from metallurgical processes other than those mentioned in 16 11 03 | Low |
| 16 11 06 | linings and refractories from non-metallurgical processes others than those mentioned in 16 11 05 | Low |
| 17 | Construction and demolition wastes (including excavated soil from contaminated sites) |  |
| 17 01 | Concrete, bricks, tiles and ceramics |  |
| 17 01 01 | concrete | Low |
| 17 01 02 | Bricks | Low |
| 17 01 03 | Tiles and ceramics | Low |
| 17 01 07 | Mixtures of concrete, bricks, tiles and ceramics other than those mentioned in 17 01 06 | Low |
| 17 02 | Wood, glass and plastic |  |
| 17 02 01 | Wood | Med |
| 17 02 02 | Clean glass only | Low |
| 17 02 03 | Plastic | Med |
| 17 03 | Bituminous mixtures, coal tar and tarred products |  |
| 17 03 02 | bituminous mixtures other than those mentioned in 17 03 01 | Low |
| 17 04 | metals (including their alloys) |  |
| 17 04 01 | Copper, bronze, brass | Low |
| 17 04 02 | Aluminium | Low |
| 17 04 03 | Lead | Low |
| 17 04 04 | Zinc | Low |
| 17 04 05 | Iron and steel | Low |
| 17 04 06 | Tin | Low |
| 17 04 07 | Mixed metals | Low |
| 17 04 11 | Cables other than those mentioned in 17 04 10 | Med |
| 17 05 | Soils (excluding soils from excavated sites), stones and dredgings |  |
| 17 05 04 | Soils and stones including chalk other than those mentioned in 17 05 03 | Low |
| 17 05 08 | Track ballast other than those mentioned in 17 05 07 | Low |
| 17 06 | Insulation materials and asbestos-containing construction materials |  |
| 17 06 04 | insulation materials other than those mentioned in 17 06 01 and 17 06 03 | Low |
| 17 08 | Gypsum based construction material |  |
| 17 08 02 | Gypsum only other than that mentioned in 17 08 01 | Low |
| 17 09 | other construction and demolition wastes |  |
| 17 09 04 | mixed construction and demolition wastes other than those mentioned in 17 09 01, 17 09 02 and 17 09 03 | Low |
| 19 | Wastes from waste management facilities, off-site waste water treatment plants and preparation of water intended for human consumption/industrial use |  |
| 19 01 | wastes from incineration or pyrolysis of waste |  |
| 19 01 02 | ferrous materials removed from bottom ash | Low |
| 19 01 12 | bottom ash and slag other than those mentioned in 19 01 11 | Low |
| 19 01 18 | pyrolysis wastes other than those mentioned in 19 01 17 | Low |
| 19 01 19 | sands from fluidised beds | Low |
| 19 02 | wastes from physico/chemical treatments of waste (including dechromatation, decyanidation, neutralisation) |  |
| 19 02 03 | premixed wastes composed only of non-hazardous wastes | Med |
| 19 02 10 | combustible wastes other than those mentioned in 19 02 08 and 19 02 09 | Med |
| 19 04 | vitrified waste and wastes from vitrification |  |
| 19 04 01 | vitrified waste | Low |
| 19 05 | Wastes from aerobic treatment of solid wastes |  |
| 19 05 01 | non-composted fraction of municipal and similar wastes | Low |
| 19 05 02 | non-composted fraction of animal and vegetable waste | Med |
| 19 05 03 | Off-specification compost (compost from source segregated biodegradable waste only) | Med |
| 19 12 | Wastes from the mechanical treatment of waste (for example sorting, crushing, compacting, pelletising) not otherwise specified |  |
| 19 12 01 | Paper and cardboard | Med |
| 19 12 02 | Ferrous metal | Low |
| 19 12 03 | Non-ferrous metal | Low |
| 19 12 04 | Plastic and rubber | Med |
| 19 12 05 | Glass | Low |
| 19 12 07 | Wood other than that mentioned in 19 12 06 | Med |
| 19 12 08 | Textiles | Med |
| 19 12 09 | Minerals (for example sand, stones) | Low |
| 19 12 10 | Combustible waste (refuse derived fuel) | Med |
| 19 13 | Wastes from soil and groundwater |  |
| 19 13 02 | Solid wastes from soil remediation other than those mentioned in 19 13 01 | Low |
| 20 | Municipal wastes (household waste and similar commercial, industrial |  |
| 20 01 | Separately collected fractions |  |
| 20 01 01 | Paper and cardboard | Med |
| 20 01 02 | Clean glass only | Low |
| 20 01 08 | Biodegradable kitchen and canteen waste | Med |
| 20 01 10 | Clothes | Med |
| 20 01 11 | Textiles | Med |
| 20 01 34 | batteries and accumulators other than those mentioned in 20 01 33 | Med |
| 20 01 36 | discarded electrical and electronic equipment other than those mentioned in 20 01 21, 20 01 23 and 20 01 35 |  |
| 20 01 38 | wood other than that mentioned in 20 01 37 | Med |
| 20 01 39 | Plastics | Med |
| 20 01 40 | Metals | Low |
| 20 01 41 | Wastes from chimney sweeping | Low |
| 20 02 | Garden and park wastes (including cemetery waste) |  |
| 20 02 01 | Biodegradable waste | Med |
| 20 02 02 | Soils and stones | Low |
| 20 03 | Other municipal wastes |  |
| 20 03 01 | Mixed municipal waste | High |
| 20 03 02 | Waste from markets | Med |
| 20 03 03 | Street cleaning residues | Low |
| 20 03 07 | Bulky waste | Med |