[image: image40.png]pH Control Chart

8.0 -

75

7.0

6.5

6.0 T T T

22/082082/0308203213% 1121313132188 38

——8P ——=+8SW12 -—=-DP2




[image: image41.png]Amm-N Control Chart

T o
i

(mg/1)

22/0482/082/032/082032/1321 31313138 d 38

e==CL ——-SP ——-SW12 —=-DP2





[image: image42.png](ne/1)

2000
1800
1600
1400
1200
1000
800
600
400
200

B Control Chart

220d2/082/032/082032182/13%/13%132132/1321813214/19

e O e CON ——SP ——SW12 —=—DP2




[image: image43.png](ne/1)

90

Cr Control Chart

80
70

60

50
40

30

20
10 +

04

L20d200d20320820821321§21 324132132482 34824

s G| @ CON ——SP —+—SW12 —=—DP2




[image: image44.png](ne/1)

60

50

40

30

20

10

V Control Chart

2208208208208 208%1521 #2131 d2d8 3 d e

s G| e CON —0— SP ——SW12 —=—DP2






Summary

This document gives details on the performance of Aberthaw Quarry Ash Disposal Site over 2017, as required by condition 4.2.1 of the site’s Environmental Permit (EP), BP3339BH.
CONTENTS

41.
Operational Update


42.
Review of Results for Emission Monitoring


42.1.
Groundwater Quality Review


112.2.
Surface Water Quality Review


163.
Annual Improvement Targets Summary


174.
Annual Production/Treatment Data


175.
Contamination/Decontamination of Site


176.
Topographical Survey


177.
Landfill Capacity


188.
Waste Acceptance Compliance Testing


20Appendix A.
Groundwater and Surface Water Monitoring Locations


22Appendix B.
Groundwater and Surface Water Quality


27Appendix C.
Topographical Survey





1. Operational Update

Aberthaw Quarry Ash Disposal Site (AQADS) is being constructed and filled with Pulverised Fuel Ash (PFA) in four distinct phases (see Appendix A). Phase 1 was constructed in 2008, filled between Quarter 4 2008 to Quarter 4 2010 and then capped and hydroseeded in Spring 2011. Phase 2 was constructed in 2009/10 with filling commencing from Quarter 4 2010. Phase 2 East was filled until Quarter 3 2013 before being capped and hydroseeded whilst Phase 2 West was filled until Quarter 4 2014 before being capped and hydroseeded. Phase 3A (east) was constructed in 2012/13 with filling commencing in Quarter 3 2013 and remained the working phase throughout 2014 and 2015. The construction of Phase 3B (west) was completed in 2014 with filling commencing in Quarter 2 2015. In 2016, Phase 3A and Phase 3B remained as the working phases. In quarter 1 of 2017 ash disposal continued into phase 3B as usual until the last week of March when the Power Station transitioned to ‘Summer Cold’ status i.e. zero electrical generation and hence zero ash production. The Summer Cold period lasted until November after which a small volume of electrical generation occurred which required circa 2.5kt of ash to be deposited in the Quarry in December.         

2. Review of Results for Emission Monitoring
2.1. Groundwater Quality Review
Monitoring Objective

To carry out routine monitoring of groundwater to monitor the performance of the ash disposal site by measurement of absolute levels and concentrations and trends relative to relevant criteria including background levels and concentrations, control levels and compliance limits.  

Number and Location of Monitoring Points

A summary of the monitoring boreholes is provided in Table 1 below and the locations are shown in Appendix A. In January 2015, borehole improvement works were completed to improve water sampling. E05-03 and E06-01were re-drilled (new details provided in Table 1) and the top hat cover was replaced on E06-05. In addition, a new borehole was installed above Phase 3B, E15/1 to improve the understanding of groundwater quality potentially flowing into the site from the south-east. In total, there are 12 boreholes in natural ground, all completed in the Porthkerry Member limestone. 
Groundwater flow beneath the ash disposal site is directed towards the cement work lagoons and the River Thaw to the west. Hence, monitoring boreholes, E09-01A, E09-01B, E09-02A and E09-02B on the north-eastern site boundary (approximately 200m apart) are upgradient. Borehole E15/1 on the south site boundary is also upgradient.
Monitoring boreholes along the western site boundary (E05-03, E05-04 and E06-01) with an average spacing of 100m are downgradient of the Pulverised Fuel Ash (PFA) disposal area (Phase 1 and 2). Along the south-western site boundary, two of the monitoring boreholes with an average spacing of 100m (E06-02 and E06-03) are downgradient of the current active PFA disposal area (Phase 3A & 3B) and a future filling phase (Phase 4). Whilst the two remaining boreholes (E06-04 and E06-05) with an average spacing of 100m may be downgradient of a future filling phase (Phase 4).

Table 1: Summary of Monitoring Boreholes
	Monitoring Borehole
	Formation

Sampled
	Lithology Type – Natural (N) 
	Response Zone Depth (m b GL)
	Designation

	E09-01A
	Limestone
	N
	18-24
	Upgradient

	E09-01B
	Limestone
	N
	24-30
	Upgradient

	E09-02A
	Limestone
	N
	21-27
	Upgradient

	E09-02B
	Limestone
	N
	27-33
	Upgradient

	E15-1
	Limestone
	N
	17-29
	Upgradient

	E05-03
	Limestone
	N
	3 - 15
	Downgradient 
Phase 1&2 Active Area

	E05-04
	Limestone
	N
	2.5 - 20
	Downgradient 

Phase 1&2 Active Area

	E06-01
	Limestone
	N
	3 - 15
	Downgradient 

Phase 1&2 Active Area

	E06-02
	Limestone
	N
	2 - 10
	Downgradient 

Phase 3A & 3B Active Area

	E06-03
	Limestone
	N
	2 - 10
	Downgradient 

Phase 3A & 3B Active Area

	E06-04
	Limestone
	N
	2 - 10
	Downgradient 

Future Filling Phases

	E06-05
	Limestone
	N
	2 – 8
	Downgradient 

Future Filling Phases

	m b GL – metres below ground level


Monitoring Measurements

The groundwater monitoring analytical suite contains a range of parameters which are monitored on a quarterly basis along with the groundwater level and standard field measurements in accordance with the Environmental Permit. An independent external contractor is responsible for the sampling of the groundwater boreholes and an independent external laboratory is responsible for the analysis of the samples. There have been no changes to the contractor for the groundwater sampling and one change to the analytical laboratory from Q2 2010. Table 2 summarises the changes to the groundwater sampling method since monitoring began to improve the sample quality.

Table 2: Summary of Groundwater Sampling Methods
	Monitoring Borehole
	Purge Strategy
	Purge Equipment
	Date From
	Date To

	E09-01A, E09-01B, E09-02A, E09-02B, 

E05-04
	1 x Well volume
	Bailer
	Quarter 1 2006
	Quarter 2 2013

	
	Low flow steady state
	Submersible pump
	Quarter 3 2013 
	---

	E05-03
	1 x Well volume
	Bailer
	Quarter 1 2006
	Quarter 3 2012

	
	1 x Well volume
	Inertial pump
	Quarter 4 2012 
	Quarter 2 2013

	
	Low flow steady state
	Submersible pump
	Quarter 3 2013
	---

	E06-01
	1 x Well volume
	Bailer
	Quarter 1 2006
	Quarter 2 2012

	
	1 x Well volume
	Inertial pump
	Quarter 3 2012 
	Quarter 2 2013

	
	3 x Well volume
	Inertial pump
	Quarter 3 2013 
	Quarter 4 2014

	
	Low flow steady state
	Submersible pump
	Quarter 3 2013 
	Quarter 1 2015

	E06-02, E06-03
	1 x Well volume
	Bailer
	Quarter 1 2006
	Quarter 2 2012

	
	1 x Well volume
	Inertial pump
	Quarter 3 2012 
	Quarter 2 2013

	
	3 x Well volume
	Inertial pump
	Quarter 3 2013 
	Quarter 3 2014

	
	Low flow steady state
	Submersible pump
	Quarter 4 2014
	---

	E06-04, E06-05
	1 x Well volume
	Bailer
	Quarter 1 2006
	Quarter 2 2013

	
	3 x Well volume
	Inertial pump
	Quarter 3 2013 
	---


Figure 1 shows the recorded groundwater elevations for the previous 11 years which vary between +17 (E05-03) to +35m OD (E05-02B). Upgradient groundwater elevations are characterised by larger amplitude seasonal water level fluctuations with annual winter influxes of rainfall recharge. Downgradient groundwater elevations fluctuate only slightly due to effect of dewatering from the Quarry which maintains groundwater at near-constant elevations. 
Figure 1: Groundwater Hydrograph 
	[image: image45.png](mg/1)

1500

art
Control Ch
so4

1250

1000

750

500

250 -+

2216
12181
12/1 5

1216

115

1214

1215

12/15

s

1214

1204

1204

12/0612/05

25

DP2
12 —o—

SP ——SW

-

CON

CL e







Figure 2 shows the general groundwater quality for the major ions in each of the groundwater boreholes. Natural groundwater quality varies between upgradient and downgradient groundwater. Calcium is depleted in downgradient boreholes, E05-03, E05-04, E06-01 and E06-02 and correlated with elevated sodium, suggesting ion exchange reactions are occurring along the groundwater flow path. Whilst in downgradient boreholes, E06-03, E06-04 and E06-05, major ion chemistry is distinctly different with elevation of calcium, magnesium and sulphate, suggesting a natural geological or quarry-related source in or upgradient of this area. 
Figure 3 shows the groundwater control charts with concentrations of all downgradient boreholes plotted as well as the average upgradient concentration (representing concentrations in boreholes E09-01A, E09-01B, E09-02A and E09-02B i.e. background groundwater quality). It should be noted that the compliance limits apply to boreholes E05-03, E05-04 and E06-01 whilst the control levels (where defined) apply to all downgradient boreholes. An exceedance is defined as a result above the compliance limit or control level for 3 consecutive sampling events. 

In 2017 there was a continued exceedance of the compliance limit and control level for Molybdenum at borehole E05-03, however the upward trend observed since 2012 seems to have plateaued somewhat in 2017 with results fluctuating between 1160 and 1610ug/l, this may be as a result of the mitigating actions carried out in 2015 or the ground water reaching an equilibrium with the source. The slightly elevated Cadmium result in E05-03 in Q4 2017 is considered an anomaly as the previous 3 quarterly results were below the method of detection limit, however there was a previous single high result for Cadmium in Q3 2016 and as such this parameter will continue to be monitored. The elevated Molybdenum result for E06-01 seen in Q4 2016 has not been repeated in 2017 with all results well below the compliance limit and control level. Other key points to note are:-
· Naturally elevated Sulphate concentrations in E05-03, E06-04 and E06-05 above 400mg/l.
Figure 4 shows the control chart for molybdenum for E05-03 and the two other boreholes closest to it, E05-04 and E06-01 as well as the surface water monitoring points (note there are no surface water compliance limits or control levels for molybdenum). The boreholes are located to the west of and adjacent to Phase 1 and are downgradient of active filling operations. Natural background concentrations of molybdenum in the Porthkerry Formation are <3µg/l and the average pre-filling concentration for the cement works lagoon (SW12) is 3µg/l.  
Figure 4: Molybdenum concentrations
	
	



[image: image1]      
[image: image2]
Molybdenum concentrations in E05-03 have been increasing since January 2012, around a year after Phase 1 was completed, which suggests the source is unlikely to be from the deposited PFA. After reviewing the 2016 data it appeared there was a co-association of increasing concentrations in other indicative PFA leachate parameters; boron, sulphate and ammoniacal-nitrogen, suggesting PFA is the source of contamination. During site investigations in 2014, three possible sources were identified; discharges from the wheel wash pipe into an unlined ditch close to the borehole; surface water discharges of eroded PFA areas around the wheel wash pipe into the unlined ditch; and/or; leakage from adjacent cement works lagoon. In 2015, the wheel wash discharge pipe was re-routed into Settlement Pond 1, the unlined ditch cleaned out and the eroded areas smoothed. Since the improvements, molybdenum concentrations continued to increase for over 14 months/5 sampling rounds) until Q1 2017 when the results decreased for two sampling rounds, increased for Q3 and then decreased again for Q4 which suggests levels have plateaued, also this trend appeared to be followed by Boron, Ammoniacal Nitrogen and Sulphate which are the other indicative PFA leachate species, lending weight to the hypothesis that the remedial works in 2015 have mitigated the contamination. Further monitoring will be required to confirm if levels have stabilised, further investigation will be undertaken as part of the hydrogeological risk assessment review in 2018.
In borehole E05-04, molybdenum concentrations were approximately double the natural background concentrations until March 2014. Since then concentrations have increased moderately up to 59µg/l and there appears to be an increasing trend suggesting the source of contamination may be spreading. Prior to 2015, the molybdenum concentrations in E06-01 have consistently reflected the natural background concentrations, since February 2015, results have been sporadically above the natural background concentrations up to 67µg/l, but levels have decreased back to historic levels in 2017, thus suggesting the source of contamination has not impacted this borehole. There is no co-association of increasing concentrations in other indicative PFA leachate parameters in either E05-04 or E06-01. As in E05-03, molybdenum concentrations in the settlement ponds (SP) have been increasing since January 2012, however, since 2013, concentrations are characterised by large amplitude seasonal fluctuations, with the highest concentrations in the summer and the lowest in the winter. This seasonal fluctuation is reflected in DP2 which collects surface water and groundwater from the site, suggesting the source of contamination is intermittent. The water from the settlement ponds is discharged periodically into the cement works lagoon (SW12) and molybdenum concentrations have been rising steadily since January 2012 to levels similar to those in E05-03.
Figure 2: General Groundwater Quality Charts 

	Upgradient Boreholes
	Downgradient Boreholes Phase 1/2
	Downgradient Boreholes Phase 3/4
	Downgradient Boreholes Future 
Phase

	
[image: image3]All analytes low and concentrations steady.
	
[image: image4]All analytes low but fluctuating.
	
[image: image5]All analytes low but increasing except HCO3; Cl from Jan-12; Mg/K/Ca from Sep-14; and; SO4/Na from Aug 2015. 
	
[image: image6]All analytes low but fluctuating, Mg/SO4 decreasing then increasing since Sept-14.
	
[image: image7]All analytes low except SO4 increasing and 
from Nov-14 Cl, Mg, Na and K increasing.

	
[image: image8]All analytes low and concentrations steady.
	
[image: image9]All analytes low but fluctuating, spike Mg 09-11.
	
[image: image10]All analytes low, concentrations steady, Ca depleted, Cl increasing from Feb-15.
	
[image: image11]All analytes low except Mg and SO4 elevated. Q4 2017 Cl spike suspect anomaly
	
[image: image12]All analytes low except SO4 elevated.

	
[image: image13]All analytes low, Mg & Na higher than other upgradient boreholes.
	
	
[image: image14]All analytes low, concentrations steady, Ca depleted.
	
	


Figure 3: Control charts for groundwater boreholes 

(CL – Compliance Limit, CON – Control Level, 0 – result at Method Detection Limit, Duplicate results also plotted)

	
[image: image15]
	
[image: image16]

	
[image: image17]         
	
[image: image18]

	
[image: image19]         
	 
[image: image20]

	
[image: image21]           
	 
[image: image22]

	
[image: image23]            
	 
[image: image24]


A summary of the average groundwater quality for all monitoring parameters between 2006 and 2017 is provided in Appendix B with a comparison of pre- and post-fill concentrations. The key trends in the data have been discussed above, however, it can be summarised that there may be some low level contamination from fugitive emissions of PFA, which is considered to have not significantly impacted the groundwater receptors.
The difference in pH between field and laboratory measurements in 2017 was less than 0.5 pH units (apart from one clearly wrong figure of 18.24 in E09-02B in Q3) which indicates stable sample conditions. For Electrical Conductivity the difference was between 0-25% with field measurements consistently higher. A change greater than 10% may indicate a change in sample conditions and therefore for some samples precipitation of solids between sampling and analysis may be occurring. Yet Major ion balances were all within +/- 5% suggesting precipitation of solids is minimal. Duplicate samples collected during 2017 showed good repeatability and were within the expected laboratory error of +/- 20%. 
2.2. Surface Water Quality Review

Monitoring Objective
To carry out routine monitoring of surface water to;
· monitor the performance of the ash disposal site by measurement of absolute levels and concentrations and trends relative to relevant criteria including background concentrations and control levels; and; 

· identify and quantify effects on surface water receptors.  

Number and Location of Monitoring Points

A summary of the surface water monitoring points is provided in Table 3 below and the locations are shown in Appendix A. As detailed in a letter to NRW dated 13thJune 2014 a new surface water monitoring point has been added, DP2, to monitor the composition of water from the under-drainage. Routine monitoring at DP2 began in May 2014. 

Table 3: Summary of Surface water monitoring points
	Monitoring Point
	Description
	Direction from site
	Designation

	SW12
	East shore of cement works lagoon in NW area
	West
	Surface water Receptor

	Settlement Ponds (SP)
	Two concrete ponds collecting groundwater and surface water
	South-west
	

	DP2
	Surface water and groundwater drainage channel at base of Phase 1 and 2
	West within site
	


A proportion of the upstream and underlying groundwater will be collected in the groundwater drainage layer and directed towards the two settlement ponds along with any water that has infiltrated through the PFA and the barrier/attenuation layer. Surface water from runoff is also directed into the two settlement ponds via a series of perimeter ditches and toe drains. The settlement ponds are constructed on the quarry floor, contained by concrete and butyl lined 3m high bunds and are designed to allow suspended solids to settle out before the water is discharged through penstocks into the nearby cement works lagoon (SW12).

Monitoring Measurements

The surface water monitoring analytical suite contains a range of parameters which are monitored on a quarterly basis for SW12 and a monthly basis for the SP and DP2, in accordance with the Environmental Permit. Trained in-house operatives are responsible for the sampling of the SP and DP2 and an independent external contractor is responsible for the sampling of SW12. An independent external laboratory is responsible for the analysis of the samples. There was a change to the analytical laboratory from September 2009 for the SP surface water analysis and from Q2 2010 for the SW12 surface water analysis. 
Figure 5 shows the general surface water quality for the major ions. Calcium, magnesium and sulphate concentrations appear naturally elevated in the cement works lagoon and the settlement ponds i.e. prior to any PFA deposition, and are at similar concentrations to those in the downgradient boreholes, E06-03, E06-04 and E06-05, suggesting a natural geological or quarry-related source upgradient of this area. Concentrations appear to be seasonably variable in the settlement ponds and the cement works lagoon with highs in July to December and lows in February to June except for HCO3 with lows in July to December and highs in February to June. When routine monitoring began in DP2 in May 2014 this seasonal pattern in concentrations was also evident. The seasonal pattern is much more marked in 2013-2017 with much higher chloride concentrations than seen previously. It is not clear where the source of chloride is coming from and this will be investigated during the hydrogeological risk assessment review in 2018.

Figure 5: General Surface Water Quality Charts
	
[image: image25]Fluctuations in SO4, Na & Cl with high concentrations in summer and low concentrations in winter.
	
[image: image26]From 2013 fluctuations in Mg, K, Ca, SO4, Na & Cl  with high concentrations in summer and low concentrations in winter and HCO3 with low concentrations in summer and high concentrations in winter.  
	
[image: image27]From 2013 fluctuations in Mg, K, SO4, Na & Cl with high concentrations in summer and low concentrations in winter.

	
[image: image28]
	
[image: image29]
	


Figure 6 shows the surface water control charts. It should be noted that the compliance limits apply to the discharge from the settlement ponds whilst the control levels (where defined) apply to both the discharge from the settlement ponds and SW12. An exceedance is defined as a result above the compliance limit or control level for 3 consecutive sampling events. 

In 2017, there were no exceedances of the compliance limit or control level for any critical parameter, except for sulphate and ammoniacal nitrogen. SP sulphate concentrations exceeded the compliance limit of 400mg/l for every month except for the April result. A temporary approval of the elevated discharge is in place with NRW on the basis of no environmental impact and the understanding that the elevated concentrations are being caused by drainage into the site from the south-east. This will be reviewed as part of the hydrogeological risk assessment review in 2018. Ammoniacal nitrogen concentrations exceeded the compliance limit of 0.6mg/l in Jan, Feb and Dec 2017 although sufficient oxidation or stripping appears to take place by the time the discharge passes to the cement works lagoon as concentrations are low and not increasing. Ammonia levels will be reviewed as part of the hydrogeological risk assessment review in 2018.
In general, Figure 6 shows that there are no increasing trends in critical parameter concentrations except for sulphate as discussed above and that although concentrations of critical parameters have been variable over time there appears to be no impact on the water quality within the cement works lagoon, SW12 into which the settlement ponds discharge. Other key points to note are:

· variable chromium concentrations in SP (between 1µg/l and 30µg/l) and DP2 (between 10µg/l and 80µg/l), although concentrations in DP2 are decreasing to around 5µg/l.       

· variable boron concentrations in SP (between 129µg/l and 975µg/l) and DP2 (between 241µg/l and 970µg/l).       

· variable ammoniacal nitrogen concentrations in SP (between 0.5mg/l and 1.52mg/l) and DP2 (between 0.5mg/l and 6.2mg/l). 

During 2015, works to improve surface water management included the re-profiling of drainage ditches, concrete lining of some of the key surface water ditches and removal of small PFA slippages.    
A summary of the average surface water quality between 2006 and 2017 is provided in Appendix B with a comparison of pre- and post-fill concentrations. The key trends in the data have been discussed above, however, it can be summarised that there may be some low level contamination from fugitive emissions of PFA, which is considered to have not significantly impacted the surface water receptors. 

Figure 6: Surface Water Control Charts 
(CL – Compliance Limit, CON – Control Level, 0 – result at Method Detection Limit, Duplicate results also plotted)

	[image: image46.png](ug/1)

50

40

30

As Control Chart

220820807 /08 /04 /18 /1717181818181 7 /1810

(| e===CON ——SP —0—-SW12 —=-DP2





	
[image: image30]

	
[image: image31]
	
[image: image32]

	
[image: image33]
	
[image: image34]

	
[image: image35]
	
[image: image36]


3. Annual Improvement Targets Summary

RWE Generation has decided to move to a single central ISO14001 certification in which Aberthaw Power Station is included and as such continues to maintain an ISO 14001 Certification for the “Generation of electricity, by the combustion of fossil fuel and biomasses, together with the associated sale or disposal of ash”. The station had a surveillance visits by Lloyds Register Quality Assurance during 2017 to facilitate the new certification and no non-conformities were identified. Table 4 provides details of the improvement targets for 2017 and the performance against those targets.

Table 4: Environmental Improvement Plan 

	Objective
	Target
	Target Date
	Responsible Person

	Maintain a high level of environmental compliance
	<3 Environmental incidents resulting in a justified complaint.
	End 2017
	All employees

	
	0 Category 1 or 2 Environmental Permit non-compliances. 

(A non-compliance that could have a major or significant environmental effect)
	End 2017
	All employees

	
	<3 Category 3 or 4 Environmental Permit non-compliances

(A non-compliance that could have a minor environmental effect or no potential environmental effect)
	End 2017
	All employees

	
	Complete response to Environmental Permit Improvement Condition 21 - Impact of Flue Gas Desulphurisation on Marine Environment Report. 
	01/08/2017
	Environmental Compliance Engineer

	
	Complete response to Environmental Permit Improvement Condition 23 – Emissions to Water Monitoring Review for Trace Elements. 
	31/12/2017
	Environmental Compliance Engineer

	
	Reduce NOx emissions/GWhr by implementing the firing of higher volatile matter coal.
	End 2017
	Engineering Manager

Production Manager

	
	Obtain the Environmental Permit Variation for the high volatile matter coal conversion.
	Jul 2017
	Commercial Manager

	Optimise the use of resources and minimise waste 


	Water
	
	

	
	<140m3/GWh process water (Ely Wells/St Lythan’s supplement)
	End 2017
	All employees

	
	Complete installation of water meter on the LP main.
	Oct 2017
	Station Chemist

	
	Waste 
	
	

	
	<15 segregation non-compliances

(>10% wrong material in the skip/waste causing safety or environmental hazard)
	End 2017
	All employees

	Engage with our local communities and be responsive to concerns and feedback regarding our activities
	Provide response to public enquiries and complaints within 48hrs of normal office hours. 
	Ongoing
	Environmental Compliance Engineer

	
	
	
	

	
	Hold a Local Liaison Committee.
	Oct 2017
	Station Manager

	Reduce the carbon intensity of electricity generated
	To review and meet the business plan targets for thermal efficiency.  
	End 2017
	Section Head Performance & Commercial

	Drive continuous improvements in standards of environmental management
	Implement the transition process for updating the EMS to the revised ISO14001:2015 Standard and incorporating into the RWE Generation UK EMS.
	End 2017
	Commercial Manager

	
	Complete a review of the containment and attenuation design, impact assessment and all elevated parameters in groundwater and surface water as part of the hydrogeological risk assessment review for Aberthaw Quarry Ash Disposal Site.
	30/06/2017
	Environmental Compliance Engineer

	
	Ensure all staff and residential contractors (managers and first line supervisors) new to site in 2017 have completed the environmental awareness training program.
	End 2017
	Section Heads/Line Managers/

Technical Officers

	
	Review options for the bund planting around the northern laydown area. 
	Q4 2017
	Environmental Compliance Engineer

	
	Install oil in water monitor in the site drainage system at P2.
	Q2 2017
	Station Chemist


4. Annual Production/Treatment Data

Table 5: Annual Production/Treatment Data(Table S5.2 EP) 

	Parameter
	Value
	Unit

	Surface water disposed off site
	0


	m3/yr

	Groundwater disposed off site
	0


	m3/yr


5. Contamination/Decontamination of Site

There have been no incidents or emissions which may have caused any site contamination during 2017, and, therefore, no requirement to decontaminate the site during 2017.
6. Topographical Survey

The last topographical survey to ordnance datum was carried out in September 2016 for Phase 3A and 3B which is shown in Appendix C.    

7. Landfill Capacity

Table 6 below details the amount of PFA deposited at Aberthaw Quarry Ash Disposal Site during 2017 as reported to Natural Resources Wales via the Waste Return Form. The total amount deposited is well below the permitted annual waste input limit of 650,000 tonnes. It is estimated that around 2,493,912m3 of void capacity remains (Phases 1–4). 

 Table 6: PFA Deposited 
	Reporting Period
	PFA Deposited

(tonnes)

	1st January – 31st December 2017
	141,014


8. Waste Acceptance Compliance Testing

Aberthaw Quarry Ash Disposal Site is a mono-landfill site which is under the direct operational control of Aberthaw Power Station.  All the ash is transported directly from the Power Station using lorries. 

The exact composition of PFA is dependent upon the composition of the fuel utilised by Aberthaw Power Station.  RWE has well established procedures which control the quality of fuel supplied to its stations.  The coal purchased by RWEST for Aberthaw is only from an approved ‘matrix’ for the site (i.e. a list of named coals specifically approved for use at Aberthaw).  Any new fuels undergo a rigorous fuel assessment process before trial/use on site to ensure they meet the mandatory fuel specifications and safety requirements of the station.

Table 7 summarises the analytical data obtained for leachate tests performed on composite samples of conditioned PFA from Aberthaw Power Station between 2012 and 2017. The CEN two-stage method for leachate analysis was used (BS EN 12457-3:2002 Characterisation of waste – Leaching – Compliance test for leaching of granular waste materials and sludge’s of which Part 3). 

Table 7: Summary of 10:1 Leachate Calculated Results (mg/kg) 
	Period
	Jan-17
	Apr-12 to Jan-17
	

	Analyte:
	Latest Result
	Minimum
	Mean
	Maximum
	Number of results

	Aluminium as Al (Dissolved)
	8.1
	2.4
	21.9
	75.4
	15

	Ammoniacal Nitrogen as N
	156.6
	4.2
	83.5
	158.1
	15

	Antimony as Sb (Dissolved)
	0.192
	0.020
	0.163
	0.256
	15

	Arsenic as As (Dissolved)
	2.449
	0.077
	1.907
	3.313
	15

	Barium as Ba (Dissolved)
	1.4
	0.1
	2.5
	5.9
	15

	Boron as B (Dissolved)
	12.1
	0.7
	12.8
	17.7
	15

	Bromide as Br
	36.3
	0.6
	71.5
	293.5
	15

	Cadmium as Cd (Dissolved)
	0.0010
	0.0004
	0.002
	0.0056
	15

	Chromium as Cr (Dissolved)
	0.19
	0.01
	0.3
	1.03
	15

	Copper as Cu (Dissolved)
	0.010
	0.004
	0.015
	0.028
	15

	Cyanide (Total) as CN
	0.5
	0.2
	0.3
	0.5
	15

	Dissolved Organic Carbon
	25.5
	2.2
	22.6
	43.3
	15

	Fluoride as F
	21.7
	2.3
	23.5
	45.1
	15

	Iron as Fe (Dissolved)
	1.16
	0.52
	1.03
	1.52
	15

	Lead as Pb (Dissolved)
	0.043
	0.013
	0.034
	0.083
	15

	Manganese as Mn (Dissolved)
	0.025
	0.006
	0.066
	0.174
	15

	Mercury as Hg (Dissolved)
	0.0019
	0.0004
	0.0057
	0.0132
	15

	Molybdenum as Mo (Dissolved)
	8.1
	0.7
	9.4
	17.8
	15

	Nickel as Ni (Dissolved)
	0.040
	0.003
	0.028
	0.062
	15

	Nitrate as N
	4.6
	2.3
	3.1
	4.6
	15

	Selenium as Se (Dissolved)
	2.8
	0.2
	2.1
	3.5
	15

	Sodium as Na (Dissolved)
	327
	9
	821
	2696
	15

	Total Dissolved Solids
	6787
	350
	8888
	21800
	15

	Total Nitrogen as N
	162.7
	5.0
	92.1
	166.0
	15

	Total Sulphur as SO4 (Dissolved)
	3745
	170
	3422
	4271
	15

	Vanadium as V (Dissolved)
	3.59
	0.40
	2.39
	3.59
	15

	Zinc as Zn (Dissolved)
	0.17
	0.01
	0.14
	0.57
	15


Appendix A.
Groundwater and Surface Water Monitoring Locations 

This page has intentionally been left blank.

Appendix B.
Groundwater and Surface Water Quality

 (Dark orange exceeds compliance limits, light orange exceeds EQS/DWS, blue exceeds background >25%)
[image: image37.emf]Response 

Zone 

Interval1

m b GL

Background - Limestone

Background - Seawater

GW EQS/DWL

GW MRV

GW CL

SW CL

E05-09_01A 18-24

E05-09_01B 24-30

E05-09_02A 21-27

E05-09_02B 27-33

E15_1 17-29

Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill

E05_03 3-15 15 11 4 1

1 1 1109 1349 #DIV/0! 0.1 37 136 3 1 7 1 38 47

E05_04 2.5-20 21 11 6 2

4 2 2123 2122 #DIV/0!#DIV/0! 6 8 4 1 5 1 39 31

E06_01 3-15 16 14 6 1

1 2 1667 1752 #DIV/0!#DIV/0! 10 7 4 1 1 1 47 30

E06_02 2-10 21 11 6 1

2 1 1113 989 #DIV/0! 0.1 89 69 3 1 5 1 86 30

Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill

E06_03 2-10 19 10 5 2

1 1 561 420 #DIV/0! 0.1 131 160 3 1 2 2 71 #DIV/0!

E06_04 2-10 17 11 4 1

1 1 58 157 #DIV/0! 0.1 147 217 3 1 5 3 55 37

E06_05 2-8 21 10 5 1

1 1 224 240 0.4 0.1 129 186 3 1 2 2 33 #DIV/0!

Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill

DP2 Phase 2 West 12 1

2 528 0.4 299 14 3 #DIV/0!

Settlement Ponds 90 1

5 296 0.3 155 8 2 55

SW12 Lafarge Lagoon 21 11 5 1

1 1 122 311 #DIV/0! 0.2 86 157 2 3 2 2 32 31

316 2 2 303 0.5

3 1 121 0.1 158 3 2 361

194

1 1 42 #DIV/0!

3 1 43 #DIV/0! 133 3 3 106

128



Average Average Average Average Average Average



Average

3 2 99

4 7

10 2800 0.4



50



50 2000 5.0



200



1



1.0



50

Average

<100

5.0 250

81

2 4166

0.6 151 3 2

50 2000



1 12 0.1

mg/l µg/l µg/l µg/l

Fe

µg/l µg/l µg/l

Cd Ca Cr Cu

Upstream Groundwater

As B

2 201

10 2000

Aquifer

5



Sb

µg/l

3

<10

200

Al

µg/l

11

256

Limestone

Downstream Active Filling Operations

Downstream Future Filling Operations

12

64

Limestone

50

14

18



Average

Limestone

21

Downstream Surface Water

#DIV/0! #DIV/0! 243 #DIV/0! 99 3 2 64


[image: image38.emf]Response 

Zone 

Interval1

m b GL

Background - Limestone

Background - Seawater

GW EQS/DWL

GW MRV

GW CL

SW CL

E05-09_01A 18-24

E05-09_01B 24-30

E05-09_02A 21-27

E05-09_02B 27-33

E15/1 17-29

Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill

E05_03 3-15

24 89 11 39 #DIV/0! 0.01 1 388 2 2 4 6 1 1 149 303 2 2

E05_04 2.5-20

4 6 6 9 #DIV/0! 0.01 2 10 2 1 4 3 2 1 241 232 4 3

E06_01 3-15

7 5 #DIV/0! 13 #DIV/0! 0.01 1 7 1 1 3 3 1 1 215 211 2 2

E06_02 2-10

56 39 18 10 #DIV/0! 0.01 3 14 4 2 10 7 2 1 109 115 2 6

Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill

E06_03 2-10

62 86 10 12 #DIV/0! 0.01 11 17 5 3 7 8 5 2 70 45 1 2

E06_04 2-10

42 63 5 25 #DIV/0! 0.01 3 5 4 3 4 24 2 1 17 39 1 2

E06_05 2-8

52 74 6 10 0.04 0.01 2 5 4 2 4 5 2 1 27 24 1 2

Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill

DP2 Phase 2 West

46 25 0.01 1721 16 36 1 426 3

Settlement Ponds

37 10 0.03 577 9 17 2 179 5

SW12 Lafarge Lagoon

23 37 2 15 0.05 #DIV/0! 3 524 2 4 6 20 2 2 23 168 2 2

2 5 2 2 28

28 2 3 24

23 52 0.01 2

2 71 0.01 3 4

2 3 17 6 8 0.02 3

6

3 1

1

Average Average



2 16 2 12 0.01 1 3

Average Average Average Average Average Average Average



60



20

3



0.03 50



0.10



50 50 1.00 200 60

<1

70 20 12 10

2



<20 <20 0.02 <30 380

16 50 0.02 21 2

mg/l µg/l mg/l mg/l µg/l µg/l µg/l µg/l

Se Mg Mn Hg Na Vn

Aquifer

Mo Ni

µg/l

3 4

9

Upstream Groundwater

Downstream Surface Water

Downstream Active Filling Operations

Limestone

Downstream Future Filling Operations

Limestone

2 5 2

K

Limestone

41 22 #DIV/0! 9 42 #DIV/0!


[image: image39.emf]Response 

Zone 

Interval1

m b GL

Background - Limestone

Background - Seawater

GW EQS/DWL

GW MRV

GW CL

SW CL

E05-09_01A 18-24

E05-09_01B 24-30

E05-09_02A 21-27

E05-09_02B 27-33

E15/1 17-29

Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill

E05_03 3-15

8.50 7.76 977 2508 462 284 178 264 0.53 0.67 0.14 0.74 0.42 1.91 33 591 1.4 1.5 16 3

E05_04 2.5-20

8.79 8.54 1010 948 564 474 79 91 0.53 0.40 0.30 0.07 0.84 #DIV/0! 31 44 6.4 5.2 19 5

E06_01 3-15

8.66 8.59 923 876 473 435 106 92 0.58 0.45 0.45 0.08 #DIV/0! 1 33 35 2.1 2.8 19 3

E06_02 2-10

8.39 7.83 1214 1000 336 287 390 276 1.09 0.52 0.72 0.57 0.60 0.59 38 38 0.6 0.5 5 4

Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill

E06_03 2-10

8.20 7.70 1224 1310 276 193 443 625 0.67 0.12 2.28 0.85 1.60 0.13 23 31 0.5 0.4 4 5

E06_04 2-10

7.99 7.57 930 1425 290 226 320 539 0.20 0.04 0.10 0.88 0.50 1.14 26 101 #DIV/0! 0.3 12 17

E06_05 2-8

8.08 7.58 1063 1237 289 204 363 578 0.21 0.07 0.30 0.18 3.30 -1.02 37 25 #DIV/0! 0.4 9 1

Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill Prefill Postfill

DP2 Phase 2 West

7.42 3469 307 486 2.17 21.68 19.82 770 0.2 1

Settlement Ponds

8.01 1701 165 380 0.10 6.55 11.63 300 0.3 2

SW12 Lafarge Lagoon

8.38 8.15 713 1635 159 151 207 380 #DIV/0! 0.08 1.16 3.21 5.09 2.27 44 266 #DIV/0! 0.2 8 3

400 0.6

Nitrate Chloride pH EC Bicarbonate Sulphate

Ammoniacal 

Nitrogen as N

Total Oxidised 

Nitrogen as N Fluoride

Total Organic 

Carbon



µS/cm mg/l mg/l mg/l mg/l mg/l mg/l mg/l mg/l

7.40 816 409 55 0.2 10.89 22 34 0.2 #DIV/0!

7.88



97 2396



16300 1.3



8.50 2500 250 400 0.3



50 250 1.5



400 1.6



Limestone

9.00

Average Average Average Average Average Average

Downstream Future Filling Operations



Average Average Average

31 0.1



Average

31 0.1



7.41 678 350 33 0.03 5.54 52

36 0.2

4

7.42 668 335 32 0.04 5.00 24

41 0.2

4

7.32 892 476 67 0.81 10.30 11

7

4

7.26 1053 474 87 0.10 24.68 25

Downstream Surface Water

Aquifer

Limestone

Upstream Groundwater

Downstream Active Filling Operations

0.29 2.65 2 36 0.2 2

Limestone

7.53 841 359 152


This page has intentionally been left blank.

Appendix C.
Topographical Survey
This page has intentionally been left blank.
2017 Annual Performance Report































































































































































































































































































































































































BRITISH ENERGY DUNGENESS B





































































































































































































































































































































































































BRITISH ENERGY DUNGENESS B





































































































































































































































































































































































































BRITISH ENERGY DUNGENESS B





































































































































































































































































































































































































BRITISH ENERGY DUNGENESS B





































































































































































































































































































































































































BRITISH ENERGY DUNGENESS B





































































































































































































































































































































































































BRITISH ENERGY DUNGENESS B





































































































































































































































































































































































































BRITISH ENERGY DUNGENESS B





































































































































































































































































































































































































Aberthaw Quarry Ash Disposal Site


Permit Number: BP3339BH


April 2018








PAGE  

[image: image47.png]Mg &K (mg/l)

110
100
EY
80
70
60
50
40
30
20
10

Settlement Ponds 2017
—8—Mg —#—K —8—Ca —+ 504 —%—Na ——Cl —B—HC03

1600

1400

/ AN - 1200

4 h-=maN

- 1000

ol u

T T T T T T T T T T T T 0
Dec Jan Fety May Apr May Jun Jui Aug Sep Oct Moy Dec “an

cl, Na, Ca, SO4 & HCO3 (mg/l)




[image: image48.png]Mg &K (mg/1)

140
130
120
110

DP2 2017

—&— Mg ——K ——Ca —+— S04 —3—Na —3—Cl —8—HC03

1600
L 1400
B
ZaN 1200
3
1000 8
H
800;
600 2
&
3
200 &
z
200 §
e e 0

Oec Jan Feb Map Apr May, Jun Jur Aug Sep Oct Noy Dec Jan




[image: image49.png]Mg &K (mg/l)

SW12

—a—Mg —#—K —8—Ca —7—-504 —3—Na ——Cl —8—HCO3

AL R SR
AV C— Vi

750
650
550
450
350
250
150
50
-50

L200d20d2032/0d20d21d1 i1 3232138825248

cl, Na, Ca, SO4 & HCO3 (mg/l)




[image: image50.png]Mg &K (mg/l)

100

Settlement Ponds

—#—Mg —8—K —8—Ca —+504 —3—Na ——Cl —B—HCO3

1600

- 1400

- 1200

F 1000
I 800
- 600
L 400
F 200

T 0

g Wog Wiy Wiy Wiy Wiy Way Wis Wis Wiy Wig

cl, Na, Ca, SO4 & HCO3 (mg/l)




[image: image51.png]Mg &K (mg/l)

DP2

——Mg —8—K ——Ca —+504 —@—Na ——Cl —8—HCO3

1600

- 1400

- 1200

- 1000

- 800
- 600
+ 400
- 200

=

22005 W05 09 W20 02 Wiy Was Wiy Was Was s,

0
Bz

cl, Na, Ca, SO4 & HCO3 (mg/l)




[image: image52.png]0.0

Amm-N Control Chart

' 7

2104208203208 2048 21§2/1 1213218441818

e C L e CON --m+-- Upstream Ave
——E05/03 —a—E05/04 —o—E06/01
—=— E06/02 —=— E06/03 —=— E06/04

—m— E06/05




[image: image53.png]Al Control Chart

100
90
80
70
= 60
E 50 >
a0
30 . s e e o
] 1 Hl
10 -
o0

220082082/03208203214%1§2131 32132188384

e C L e CON --4-- Upstream Ave
——E05/03 —a—E05/04 —O—E06/01
—=— E06/02 —a—E06/03 —— E06/04

—m=— E06/05




[image: image54.png]B Control Chart

2800
2600 5
2400 -
2200 -
2000
1800

o0 ] pRg
1400 )

1200
1000 -
800 -
600 -
400 -
200

0 B i S
22008 2082/0320820§1821§2131321§ 2182482348
— C L e CON ----- Upstream Ave
——E05/03 —a—E05/04 ——E06/01
—m— E06/02 —m— E06/03 —=— E06/04
—m— E06/05

(ne/1)




[image: image55.png]50

Cr Control Chart

40
= 30
~
E:
20
10
C g
o |55 TEeH Frfm o
2200d200d030d0dd i dndndndadaiadag
— C L e CON ---4m-- Upstream Ave
—— E05/03 —m— E05/04 —— E06/01
—o— E06/02 —m— E06/03 —— E06/04

—@— E06/05




[image: image56.png]20

V Control Chart

18

16

14

12

3 I
g 10 l I
: I
ol | w7
4
2
0
12082082%032/0§20§ 2132113131388 38
e C L e C ON ---+-- Upstream Ave
—o—E05/03 —m—E05/04 —o—E06/01
—=—E06/02 —m—E06/03 —— E06/04

—m—E06/05




[image: image57.png](mg/1)

1300
1200
1100
1000
900
800
700
600
500
400
300
200
100

e—C |
——E05/03
—a—E06/02

S04 Control Chart

s

iy —

L0d20d205208% 0132121418858

e C ON
—m—E05/04
—=—E06/03

----- Upstream Ave
—o—E06/01
—=—E06/04

—m—E06/05




[image: image58.png](ne/1)

80

70

60

50

40

30

20

10

Mo Control Chart

T

L

LI
L A

¥

= =

LY,

2210512061205 /0512051618151 7/148%151 161161

e C L

—o0—E05/03
—a—E06/02
—=— E06/05

e CON --+-- Upstream Ave
—a—E05/04 —o—E06/01
—a—E06/03 —— E06/04




[image: image59.png](ug/1)

As Control Chart

10

&

Ok N WA U O N ® W

12/0 2062070820419 %1 11518181818 211810

— CL e CON --4+-- Upstream Ave
——E05/03 —=— E05/04 ——E06/01
—=— E06/02 —=— E06/03 —=— E06/04

—a— E06/05




[image: image60.png]Hg Control Chart

0.20
0.18

0.16

0.14

=012
~

% 0.10
~ o0s

0.06

——
-
—0

0.04

0.02

=]
0.00

2200820820304 20821d21§ 1321318838

— C L ---@-- Upstream Ave  ——E05/03
—a—E05/04 ——E06/01 —=—E06/02
—=—E06/03 —— E06/04 —m—E06/05




[image: image61.png]12

o
3

(ne/1)

0.2

0.0

Cd Control Chart

Th

220082/0820320d20821d%1 #2134 §21321821821 318

— C L --4+-- Upstream Ave  —0— E05/03
—=—E05/04 ——E06/01 —=— E06/02
—a—E06/03 ——E06/04 —a&— E06/05




[image: image62.png]cl, Ca, Mg & K (mg/l)

80

70

E06/01

—=—Ca —3—Mg —8—K —5—Cl ——504 —3—Na —@—HCO3

800
700
600
500
400
300
200
100
0

L20d20d20320§20821321§21321 324 d21 8208324824

Na, SO4 & HCO3 (mg/l)




[image: image63.png]Mg, Na, K & cl (mg/l)
N
oo 3 & 8 388

E15_1 (Deep)

—B—Mg —3—Na —8—K —3—Cl —8—Ca 504 —B—HCO3

800

700
600

500

400
300

Ca, SO4 & HCO3 (mg/l)




[image: image64.png]Mg, Na, K & cl (mg/l)

E06/05

—#Mg —8—Na —8—K —B—Cl —8Ca —+ 504 —8—HC03

160

140

120

100

80

60

40 +

20

0

800
700

o o
8 8

w
8

]
8
Ca, SO4 & HCO3 (mg/l)

g

0

2205120512057 2/08 2109 72/19 121, 12157215 72/14 /1516




[image: image65.png]cl, Mg &K (mg/l)

160

140

120

100

80

60

40

20

E06/03

——Mg —#—K ——Cl ——Ca —+ 5S04 —3—Na ——HCO3

1600
1400
1200
1000
800
600
400
200
0

L0d20d20320820d2/18%1 113§ d ¢ 3

Ca, Na, SO4 & HCO3 (mg/l)




[image: image66.png]cl, Ca, Mg & K (mg/l)

E05/04

—8—Ca —#—Mg —8—K —3—Cl —+5S04 —Z—Na —@—HCO3

110
100

90
80
70
60
50
40
30

it

1100
1000
900
800
700
600
500
400
300
200
100
0

2200820620508 208 /13 218151848848 s

Na, SO4 & HCO3 (mg/l)




[image: image67.png]ep)
2B (De
-09/0:

E05

—m—Na K —=—Cl —m—Ca S04 —m—HC03
—-

—-— C

—-—

Mg

700

600

t 500
t 400
t 300

~ 200

- 100

fo
121
1216
1215
1214
1215
Z
Rz
110
12/0g
1208
12061205
2210522106

1)
g/l
03 (m,

& HC

SO4

Ca,




[image: image68.png]Mg, Na, K & cl (mg/l)

@
3

@
S

IS
S

30

E05-09/01B (Deep)

—8—Mg ——Na —8—K —5—Cl ——Ca 504 —m—HCO3

e

o
8

A
8

w
8

~
8

E,

=0

22005'2/0612/072/08'20512/15' /1121512151 4121516 21 g

Ca, SO4 & HCO3 (mg/l)




[image: image69.png]1)
(mg/
K&cl

Na,

Mg,

E06/04

3
HCO
o —a—

4 —a—

Ca 0.

K —8—

.
Na

.
Mg

e

900
800
700
600
500
400
300
200
100
0

12/16
12/15
2y
12/13

12/12

12/11

12/10

12/09

12/08

12/0612/07

12/05

1)
&HCO3 (mg/
SO4

Ca,




[image: image70.png]100
90
80
70
60
50
40
30
20
10

cl, Mg &K (mg/l)

E06/02

——Mg ——K —0—Cl —8—Ca —+ S04 ——Na —8—HCO3

700

- 600

3 - 500
\

- 400

- 300

- 200

- 100

T T T T T 0

2208208202080 % 1d 121328141818 v s

Ca, Na, SO4 & HCO3 (mg/l)




[image: image71.png]E05/03

——Mg —#—K ——Ca —+—S04 ——Na —1—Cl —B—HCO3

! 2200
2000
1800
1600

L0828 20208048 Fa R fadadad s

cl, Ca, Na, SO4 & HCO3 (mg/l)




[image: image72.png]E05-09/02A (Shallow)

—#—Mg —&—Na —#—K —0—Cl —#—Ca —+ S04 —@—HCO3

~
S

3

P

Mg, Na, K & cl (mg/l)
Noow

,_.
S

& & &

S

800
700
600
500
400
300
200
100

Seazi i Lo
2051206207208 204210121121 72/ 81516/ 71

Ca, SO4 & HCO3 (mg/l)




[image: image73.png]Mg, Na, K & cl (mg/l)

60

50

40

30

20

10

0

E05-09/01A (Shallow)

—#—Mg —Z—Na —#—K —0—C| —8—Ca —+-504 —8—HCO03

Vi [T
\ | o
ey, i = L
oo ooy

L20512/06'/05 2051 /05'%/10"%/1 715815818158 /161 1 718

Ca, SO4 & HCO3 (mg/l)




[image: image74.png](ne/1)

80

70

60

Mo Control Chart
2000

- 1800

- 1400

1200=

ne/

1000=

800

E05/03

600

400

200

0
2200d20d 203 %0d0d1d i F i vadvadvid v iaday

@mmn(C| e===CON —8—E05/04 ——E06/01 —1—E05/03




[image: image75.png](ne/1)

4000
3600
3200
2800
2400
2000
1600
1200

800

400

Mo Control Chart

of

220820207 2/080d 21511121321 #4188 ad s

e GW CL eee GW CON ——SP —0—SW12 —=—DP2




[image: image76.png]IRVWE

The energy to lead



[image: image77.png]Aberthaw Quarry Ash Disposal Site - Groundwater Elevation

--m--E09-01A/E05-01A -4u--E09-01B/E05-01B - 4m--E09-02A/E05-02A
-48--E09-02B/E05-02B -@--E15/1 —8—E05-03
—a—E05-04 —a—E06-01 —m—E06-02

E06-03 ——E06-04 —a—E06-05

BH5 - Inactive

35

33

31 Upstream BHs
destroyed

No access
upstream BHs|

29

27

25

23

21

19

Groundwater Level (mAOD)

17

15 T T T T T T T T T T T |
Dec-06 Dec-07 Dec-08 Dec-09 Dec-10 Dec-11Dec-12Dec-13 Dec-14 Dec-15Dec-16 Dec-17Dec-18

Note: Upstream monitoring wells as dotted lines.




[image: image78.png](ne/1)

Cd Control Chart

220082/0d 2032042082181 F 3 dndadvd s

—CL —+—SP ——SW12 —a—DP2




