Permit Number: 
EPR/EP3230BW

Operator: 

EnviroWales Limited
Facility:

Rassau Recycling Facility
Form Number: 
 Air1 / 15/04/2014
Reporting of emissions to air for the period from 01/01/2014 to 31/12/2014 

	Emission

Point
	Substance /

Parameter
	Emission

Limit Value
	Reference Period
	Result [1] mg/m3
	Test

Method [2]
	Sample

Date and Times [3]
	Uncertainty

[4]

	A1
	Sulphuric Acid mist
	1 mg/m3
	6 Monthly extractive sample
	0.08
	US EPA method 8
	12/12/14
11:11-12:14
	13%

	A1
	Total Particulate 


	5 mg/m3

	Extractive sample 
	21.68
	BS EN 13284-1
	19/03/14
10:30-11:35
	3%

	A1
	Cadmium and compounds (as element)
	0.5 mg/m3

	Extractive sample


	0.0023
	BS EN 14385
	12/02/14
11:00-13:06
	12%

	A1
	Copper, lead, nickel, zinc and their compounds (as metal) 
	2 mg/m3
Quarterly extractive sample
	Extractive sample


	1.08
	BS EN 14385
	19/11/14

13:30-15:36
	13%

	A1
	Antimony, tin, tellurium and their compounds (as element) 
	2 mg/m3

	Extractive sample


	0.048
	BS EN 14385
	19/11/14

13:30-15:36
	9%

	A1
	Cadmium, arsenic, thallium, selenium, and their compounds (as element) 
	0.5 mg/m3

	Extractive sample


	0.0099
	BS EN 14385
	12/02/14

11:00-13:06
	9%

	A1
	Mercury (as element) 
	0.5 mg/m3
	Extractive sample
	0.00036

	BS EN 14385
	12/02/14

11:00-13:06
	12%

	A2
	Lead and compounds (as metal) 


	2 mg/m3
	Extractive sample
	0.3
	BS EN 14385
	01/07/14
10:01-12:01
	11%

	A2
	Total Particulate 


	5 mg/m3

	Monthly CEMS average and

Extractive sample
	CEMS Averages (See graph)

1.27
	BS EN 13284-1
	25/02/14
12:15-14:15
	17%

	A2
	
	10 mg/m3
	Daily average
	
	EN 14181
	
	

	A2
	Sulphur Dioxide  


	500 mg/m3

	Monthly CEMS average and

Extractive sample 
	CEMS Averages (See graph)

60.40
	BS EN 14791
	25/02/14
13:00-14:29
	5%

	A2
	
	500 mg/m3
	Daily average
	
	EN 14181
	
	

	A2
	Hydrogen Chloride 


	10 mg/m3
	Extractive sample


	0.1
	BS EN 1911
	19/11/14
09:53-10:53
	13%

	A2
	Cadmium and compounds (as element
	0.5 mg/m3
	Extractive sample


	0.0075
	BS EN 14385
	01/07/14
13:01-12:01
	12%

	A2
	Copper, lead, nickel, zinc and their compounds (as metal) 
	2 mg/m3
Quarterly extractive sample
	Extractive sample


	0.36
	BS EN 14385
	01/07/14

13:01-12:01
	9%

	A2
	Antimony, tin, tellurium and their compounds (as element) 
	2 mg/m3

	Extractive sample


	0.019
	BS EN 14385
	01/07/14

13:01-12:01
	8%

	A2
	Cadmium, arsenic, thallium, selenium, and their compounds (as element) 
	0.5 mg/m3

	Extractive sample


	0.0098
	BS EN 14385
	01/07/14

13:01-12:01
	10%

	A2
	Mercury (as element) 
	0.5 mg/m3
	Extractive sample
	0.0057
	BS EN 14385
	01/07/14

13:01-12:01
	13%

	A2
	Dioxins and Furans (ITEQ) 


	0.1 ng/m3

	Extractive sample (min 4 hrs max 8hrs)
	0.0017 ng/m3
	BS EN 1948
	19/11/14
11:15-17:15
	20%

	A2
	Oxides of Nitrogen 


	100 mg/m3
200 mg/m3

	Monthly CEMS average and

Extractive sample 
Daily average

	CEMS Averages (See graph)

21.16


	BS EN 14792
	25/02/14
13:0014:29
	4%

	A2
	Carbon Monoxide 


	1000 mg/m3
	Monthly CEMS average and

Extractive sample
	CEMS Averages (See graph)

587.85
	EN 14181

BS EN 15058
	19/11/14
13:31-15:00
	4%

	
	
	
	
	
	
	
	

	A2
	Volatile Organic Compounds 


	50 mg/m3
100 mg/m3
	Monthly CEMS average and

Extractive sample 

Daily average
	CEMS Averages (See graph)

8.08

	BS EN 13649

EN 14181
	18/11/14
13:47-11:46
	3%

	
	
	
	
	
	
	
	

	A3
	Lead and compounds (as metal) 


	2 mg/m3
	Extractive sample 
	0.48
	BS EN 14385
	02/07/14
11:26-13:29
	12%

	A3
	Total Particulate 


	5 mg/m3
10 mg/m3
	Monthly CEMS average and

Extractive sample

Daily average
	CEMS Averages (See graph)

1.47

	BS EN 13284-1

EN 14181
	04/07/14
08:29-09:34
	17%

	
	
	
	
	
	
	
	

	A3
	Sulphur Dioxide  


	500 mg/m3

	Extractive sample


	16.9
	BS EN 14791
	12/12/14
13:01-14:30
	4%

	A3
	Hydrogen Chloride 


	10 mg/m3
	Extractive sample


	0.02
	BS EN 1911
	12/12/14
12:57-13:57
	13%

	A3
	Cadmium and compounds (as element
	0.5 mg/m3
	Extractive sample


	0.00084
	BS EN 14385
	02/07/14

11:26-13:29
	10%

	A3
	Copper, lead, nickel, zinc and their compounds (as metal) 
	2 mg/m3
Quarterly extractive sample
	Extractive sample


	0.52
	BS EN 14385
	02/07/14

11:26-13:29
	11%

	A3
	Antimony, tin, tellurium and their compounds (as element) 
	2 mg/m3

	Extractive sample


	0.026
	BS EN 14385
	02/07/14

11:26-13:29
	9%

	A3
	Cadmium, arsenic, thallium, selenium, and their compounds (as element) 
	0.5 mg/m3

	Extractive sample


	0.0086
	BS EN 14385
	11/02/14
13:35-15:46
	9%

	A3
	Mercury (as element) 
	0.5 mg/m3
	Extractive sample
	0.0085
	BS EN 14385
	11/02/14

13:35-15:46
	13%

	A3
	Dioxins and Furans (ITEQ) 


	0.1 ng/m3

	Extractive sample (min 4 hrs max 8hrs)
	0.0013 ng/m3
	BS EN 1948
	03/07/14
09:05-15:15
	20%

	A3
	Oxides of Nitrogen 


	100 mg/m3

	Extractive sample 


	3.15
	BS EN 14792
	01/07/14
14:05-15:34
	3%

	A3
	Carbon Monoxide 


	150 mg/m3
	Extractive sample 


	71.92
	BS EN 15058
	12/12/14
13:01-14:30
	4%

	A3
	Volatile Organic Compounds 
	50 mg/m3
	Extractive sample 


	15.66
	BS EN 13649
	02/07/14
12:01-13:00
	2%

	A4
	Lead and compounds (as metal) 
	2 mg/m3
	Extractive sample
	0.16
	BS EN 14385
	30/06/14
10:15-12:20
	14%

	A4
	Total Particulate 


	5 mg/m3

	Monthly CEMS average and

Extractive sample
	CEMS Averages (See graph)

3.37
	BS EN 13284-1
	30/06/14

12:32-13:36
	8%

	A4
	
	10 mg/m3
	Daily average
	
	EN 14181
	
	

	A4
	Cadmium and compounds (as element
	0.5 mg/m3
	Extractive sample


	0.00071
	BS EN 14385
	30/06/14

10:15-12:20
	9%

	A4
	Copper, lead, nickel, zinc and their compounds (as metal) 
	2 mg/m3
Quarterly extractive sample
	Extractive sample


	0.17
	BS EN 14385
	30/06/14

10:15-12:20
	13%

	A4
	Antimony, tin, tellurium and their compounds (as element) 
	2 mg/m3

	Extractive sample


	0.016
	BS EN 14385
	30/06/14

10:15-12:20
	8%

	A4
	Cadmium, arsenic, thallium, selenium, and their compounds (as element) 
	0.5 mg/m3

	Extractive sample


	0.0078
	BS EN 14385
	10/02/14
10:54-12:59
	10%

	A4
	Mercury (as element) 
	0.5 mg/m3
	Extractive sample
	0.0012
	BS EN 14385
	17/11/14
12:18-14:18
	9%

	A5
	Sulphur Dioxide  


	50 mg/m3

	Extractive sample


	34.67
	BS EN 14791
	17/11/14
13:20-14:49
	4%

	A5
	Oxides of Nitrogen 


	100 mg/m3

	Extractive sample 


	99.85
	BS EN 14792
	30/06/14
13:00-14:29
	2%

	A5
	Carbon Monoxide 


	150 mg/m3
	Extractive sample 


	22.92
	BS EN 15058
	10/02/14
14:30-15:59
	4%

	A5
	Volatile Organic Compounds 


	50 mg/m3
	Extractive sample 


	3.28
	BS EN 13649
	17/11/14
13:31-14:30
	3%

	A6
	Lead and compounds (as metal)
	2 mg/m3
	Extractive sample 
	Not operational
	BS EN 14385
	
	

	A6
	Total Particulate 


	5 mg/m3

	Extractive sample
	Not operational
	BS EN 13284-1
	
	

	A6
	Sulphur Dioxide  


	500 mg/m3

	Monthly


	Not operational
	BS EN 14791
	
	

	A6
	Oxides of Nitrogen
	100 mg/m3
	Monthly


	Not operational
	BS EN 14792
	
	

	A7
	Particulates
	No visible emission
	
	No visible emission
	
	
	

	A8
	Particulates
	No visible emission
	
	No visible emission
	
	
	


The result given is the maximum value (or the minimum value in the case of a limit that is expressed as a minimum) obtained during the reporting period, expressed in the same terms as the emission limit value. Where the emission limit value is expressed as a range, the result is given as the ‘minimum – maximum’ measured values.

Where an internationally recognised standard test method is used the reference number is given. Where another method that has been formally agreed with Natural Resources Wales is used, then the appropriate identifier is given. In other cases the principal technique is stated, for example gas chromatography.

For non-continuous measurements the date and time of the sample that produced the result is given. For continuous measurements the percentage of the process operating time covered by the result is given.   

The uncertainty associated with the quoted result at the 95% confidence interval, unless otherwise stated.

[image: image1.png]



Signed …………………………………………………………….  

Date……28/01/2015…………..   



(Authorised to sign as representative of Operator)
