Permit Reference Number:

Installation:

Operator:
Permit Reference Number: BX72821S

Installation: InBev Magor Brewery

Operator: InBev UK Ltd

Form Number: A1

Reporting of Emissions to Air for the period from 1st January 2014 to 31st December 2014
	Emission

Point
	Substance /

Parameter
	Emission

Limit Value
	Result [1]
	Test

Method [2]
	Sample

Date and Times [3]
	Accreditation/ Certification [4]
	Uncertainty

[5]

	A1
	Oxides of nitrogen as NO2
	220mg/m3 [6]
	198.3
	BS EN 14792
	10th April 12.37 – 13.37
	Mcerts MC 050056/00
	12.7

	A1
	Carbon monoxide
	None
	3.1
	BS EN 15068
	10th April 12.37 – 13.37
	Mcerts MC 050056/00
	29.1

	A1
	Oxygen
	None
	1.6
	BS EN 14789
	10th April 12.37 – 13.37
	
	

	A1
	Temperature
	None
	202
	-
	10th April 12.37 – 13.37
	
	

	A2
	Oxides of nitrogen as NO2
	220mg/m3 [6]
	190.3
	BS EN 14792
	10th April 10.06 – 11.06
	Mcerts MC 050056/00
	13.0

	A2
	Carbon monoxide
	None
	2.4
	BS EN 15068
	10th April 10.06 – 11.06
	Mcerts MC 050056/00
	29.1

	A2
	Oxygen
	None
	5.4
	BS EN 14789
	10th April 10.06 – 11.06
	
	

	A2
	Temperature
	None
	207
	-
	10th April 10.06 – 11.06
	
	

	A3
	Oxides of nitrogen as NO2
	140mg/m3 [6]
	94.5 
	BS EN 14792
	10th April 11.22 – 12.22
	Mcerts MC 050056/00
	10.3

	A3
	Carbon monoxide
	None
	3.0 
	BS EN 15068
	10th April 11.22 – 12.22
	Mcerts MC 050056/00
	29.1

	A3
	Oxygen
	None
	1.6
	BS EN 14789
	10th April 11.22 – 12.22
	
	

	A3
	Temperature
	None
	83
	-
	10th April 11.22 – 12.22
	
	

	A4
	Oxides of nitrogen as NO2
	140mg/m3 [6]
	104.4
	BS EN 14792
	10th April 14,29 – 15.29
	Mcerts MC 050056/00
	11.0

	A4
	Carbon monoxide
	None
	3.1
	BS EN 15068
	10th April 14,29 – 15.29
	Mcerts MC 050056/00
	29.1

	A4
	Oxygen
	None
	8.7
	BS EN 14789
	10th April 14,29 – 15.29
	
	

	A4
	Temperature
	None
	94
	-
	10th April 14,29 – 15.29
	
	

	A1
	Oxides of nitrogen as NO2
	220mg/m3 [6]
	Not running
	Not running
	Not running
	Mcerts MC 050056/00
	-

	A1
	Carbon monoxide
	None
	Not running
	Not running
	Not running
	Mcerts MC 050056/00
	-

	A1
	Oxygen
	None
	Not running
	Not running
	Not running
	
	

	A1
	Temperature
	None
	Not running
	Not running
	Not running
	
	

	A2
	Oxides of nitrogen as NO2
	220mg/m3 [6]
	172.1 
	BS EN 14792
	4th November 10.30 – 11.30
	Mcerts MC 050056/00
	25,2

	A2
	Carbon monoxide
	None
	1.6
	BS EN 15068
	4th November 10.30 – 11.30
	Mcerts MC 050056/00
	29.1

	A2
	Oxygen
	None
	5.8
	BS EN 14789
	4th November 10.30 – 11.30
	
	

	A2
	Temperature
	None
	206
	-
	4th November 10.30 – 11.30
	
	

	A3
	Oxides of nitrogen as NO2
	140mg/m3 [6]
	91.7
	BS EN 14792
	Not running
	Mcerts MC 050056/00
	24.2

	A3
	Carbon monoxide
	None
	1.5
	BS EN 15068
	Not running
	Mcerts MC 050056/00
	29.1

	A3
	Oxygen
	None
	1.6
	BS EN 14789
	Not running
	
	

	A3
	Temperature
	None
	86
	-
	Not running
	
	

	A4
	Oxides of nitrogen as NO2
	140mg/m3 [6]
	Not running
	Not running
	Not running
	Mcerts MC 050056/00
	-

	A4
	Carbon monoxide
	None
	Not running
	Not running
	Not running
	Mcerts MC 050056/00
	-

	A4
	Oxygen
	None
	Not running
	Not running
	Not running
	
	

	A4
	Temperature
	None
	Not running
	Not running
	Not running
	
	

	A5
	Oxides of nitrogen as NO2
	350mg/m3 [7]
	Not running
	Not running
	Not running
	Mcerts MC 050056/00
	-

	A5
	Carbon monoxide
	500mg/m3 [7]
	Not running
	Not running
	Not running
	Mcerts MC 050056/00
	-

	A5
	Oxygen
	None
	Not running
	Not running
	Not running
	
	

	A5
	Temperature
	None
	Not running
	Not running
	Not running
	
	

	A6
	Oxides of nitrogen as NO2
	350mg/m3 [7]
	Not running
	Not running
	Not running
	Mcerts MC 050056/00
	-

	A6
	Carbon monoxide
	500mg/m3 [7]
	Not running
	BS ISO 12039
	Not running
	Mcerts MC 050056/00
	-

	A6
	Oxygen
	None
	Not running
	BS ISO 12039
	Not running
	
	

	A6
	Temperature
	None
	Not running
	-
	Not running
	
	

	A5
	Oxides of nitrogen as NO2
	350mg/m3 [7]
	Not running
	Not running
	Not running
	Mcerts MC 050056/00
	-

	A5
	Carbon monoxide
	500mg/m3 [7]
	Not running
	Not running
	Not running
	Mcerts MC 050056/00
	-

	A5
	Oxygen
	None
	Not running
	Not running
	Not running
	
	

	A5
	Temperature
	None
	Not running
	Not running
	Not running
	
	

	A6
	Oxides of nitrogen as NO2
	350mg/m3 [7]
	Not running
	-
	Not running
	Mcerts MC 050056/00
	-

	A6
	Carbon monoxide
	500mg/m3 [7]
	Not running
	BS ISO 12039
	Not running
	Mcerts MC 050056/00
	-

	A6
	Oxygen
	None
	Not running
	BS ISO 12039
	Not running
	
	

	A6
	Temperature
	None
	Not running
	-
	Not running
	
	


Form Number: A1

[1] The result given is the maximum value (or the minimum value in the case of a limit that is expressed as a minimum) obtained during the reporting period, expressed in the same terms as the emission limit value. Where the emission limit value is expressed as a range, the result is given as the ‘minimum – maximum’ measured values.

[2] Where an internationally recognised standard test method is used the reference number is given. Where another method that has been formally agreed with the Agency is used, then the appropriate identifier is given. In other cases the principal technique is stated, e.g. gas chromatography.

[3] For non-continuous measurements the date and time of the sample that produced the result is given. For continuous measurements the percentage of the process operating time covered by the result is given.   

[4] The accreditation status of the equipment and/or the monitoring organisation, as appropriate, for the methods used for both sampling and analysis.

[5] The uncertainty associated with the quoted result at the 95% confidence interval, unless otherwise stated. The following uncertainties are quoted on a different basis (basis as stated) – {The basis of any other uncertainty figure needs to be stated. Where no figure is available the Agency will need to agree an appropriate uncertainty value.}

[6] Corrected to 273K, 101.3kPa, 5% oxygen, dry

[7] Corrected to 273K, 101.3kPa, 15% oxygen, dry

Signed ……Kathryn Fowler……………………………………………………….  

Date……24/1/2015…………………..   



(authorised to sign as representative of the Operator)

Permit Number: 
EPR/BX7282IS


Operator: 

Inbev UK Ltd

Facility:

Magor Brewery


Form Number: 
A2. 

Date of form 

19/07/11

Reporting of emissions to air for the period from 1st January 2014 to 31st December 2014
	Emission

Point
	Substance /

Parameter
	Emission

Limit Value
	Result [1] 
	Test

Method [2]
	Sample

Date and Times [3]
	Accreditation/certification [4]
	Uncertainty

[5]

	A8
	Oxides of nitrogen as NO2
	500
	311.4
	BS EN 14792
	6th February 13.20 -14.20
	Mcerts MC 050056/00
	51

	
	Carbon monoxide
	650
	687.7
	BS EN 15058
	6th February 13.20 -14.20
	Mcerts MC 050056/00
	68

	
	Sulphur Dioxide
	80
	5.3
	BS EN 14791
	6th February 13.20 -14.20
	Mcerts MC 050056/00
	0.7

	
	Oxides of nitrogen as NO2
	500
	419.2
	BS EN 14792
	19th August 10.35 – 11.35
	Mcerts MC 050056/00
	7.2

	
	Carbon monoxide
	650
	638.8
	BS EN 15058
	19th August 10.35 – 11.35
	Mcerts MC 050056/00
	66

	
	Sulphur Dioxide
	80
	60.7
	BS EN 14791
	19th August 10.35 – 11.35
	Mcerts MC 050056/00
	7.7

	
	Oxides of nitrogen as NO2
	500
	495.8
	BS EN 14792
	26th September 10.40 – 11.40
	Mcerts MC 050056/00
	54

	
	Carbon monoxide
	650
	657.8
	BS EN 15058
	26th September 10.40 – 11.40
	Mcerts MC 050056/00
	67

	
	Sulphur Dioxide
	80
	6.3
	BS EN 14791
	26th September 10.40 – 11.40
	Mcerts MC 050056/00
	6.3

	
	Oxides of nitrogen as NO2
	500
	433.7
	BS EN 14792
	4th December 11.13 – 12.13
	Mcerts MC 050056/00
	52

	
	Carbon monoxide
	650
	636.1
	BS EN 15058
	4th December 11.13 – 12.13
	Mcerts MC 050056/00
	67

	
	Sulphur Dioxide
	80
	97.3
	BS EN 14791
	4th December 11.13 – 12.13
	Mcerts MC 050056/00
	12.4


1. The result given is the maximum value (or the minimum value in the case of a limit that is expressed as a minimum) obtained during the reporting period, expressed in the same terms as the emission limit value. Where the emission limit value is expressed as a range, the result is given as the ‘minimum – maximum’ measured values.

2. Where an internationally recognised standard test method is used the reference number is given. Where another method that has been formally agreed with the Environment Agency is used, then the appropriate identifier is given. In other cases the principal technique is stated, for example gas chromatography.

3. For non-continuous measurements the date and time of the sample that produced the result is given. For continuous measurements the percentage of the process operating time covered by the result is given.   

4. The uncertainty associated with the quoted result at the 95% confidence interval, unless otherwise stated.

Signed …………Kathryn Fowler………………………………………………….  

Date…………24/1/2015……………..   



(Authorised to sign as representative of Inbev UK Ltd)

Permit Number: 
EPR/BX7282IS


Operator: 

Inbev UK Ltd

Facility:

Magor Brewery


Form Number: 
E2. Date of form 

19/07/11
Reporting of Energy Generation for the year 1st January 2014 to 31st December 2014
	Energy Source
	Energy Usage
	
	

	
	Quantity
	            Energy generated/m3 biogas

                        (MWh/m3)
	
	

	
	
	
	
	

	
	
	
	
	

	
	
	
	

	Electricity  generation
	1271MWh
	0.001
	

	Heat generated
	1670MWh
	0.002
	

	TOTAL
	
	
	

	
	
	
	


	Operator’s comments :
All non-compliances have been notified to the EA via telephone or e-mail.  Scheduled notifications have also been submitted.



Signed ………Kathryn Fowler…………………………………………………….  

Date……24/1/2015…………………..   



(Authorised to sign as representative of Operator)

Permit Number: 
EPR/BX7282IS


Operator: 

Inbev UK Ltd

Facility:

Magor Brewery


Form Number: 
Gas1 

Date of form 

19/07/11

Reporting of biogas quality for the year 1st July 2014 to 31st December 2014
	Parameter
	
	               Result (ppm)
	

	
	
	
	

	Hydrogen sulphide content at outlet of hydrogen sulphide scrubber
	409
	

	Hydrogen sulphide content at entry to gas engine
	409
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	

	
	
	


The result given is the maximum result over the reporting period

	Operator’s comments :

NRFW were made aware of this exceedance via a scheduled notification.  Root cause has been determined as instrumentation and signalling faults.



Signed …………………………Kathryn Fowler………………………………….  

Date………24/1/2015………………..   



(Authorised to sign as representative of Inbev UK Ltd)

Form Number: W1

Reporting of Emissions to Water (other than to Sewer) for the period from 30th September 2014 to 31st December 2014           (1st January 2014 to 31st December 2014 for metals)
	Emission

Point
	Substance /

Parameter
	Emission

Limit Value
	Result [1]
	Test

Method [2]
	Sample

Date and Times [3]
	Accreditation/

Certification [4]
	Uncertainty

[5]

	W2
	Flow
	10,000m3/day
	5801
	Continuous / cumulative – AAB flow meter
	8th November
	MCerts accredited
	+/- 1.04 %

	W2
	Flow
	126 litres/s
	63.46
	Spot – AAB flow meter
	8th November
	MCerts accredited
	+/- 1.04 %

	W2
	pH
	5 – 9 [6]
	6.5 – 8.9
	Continuous sample 
	14th October – 14th/15th and 19th October
	EA approved (IP 18)
	+/- 0.05 pH

	W2
	Temperature
	30°C
	26.7 
	Continuous sample – knick in line meter
	30th October
	EA approved (IP 18)
	+/- 1 degree C

	W2
	BOD
	200mg/l
	17
	SCA Blue Book 130
ISBN 0117522120
	15th October
	UKAS Lab 1314
	20.1%

	W2
	COD
	450mg/l
	98
	SCA Blue Book 97
ISBN 0117519154
	28th December
	UKAS Lab 1314
	5.8%

	W2
	Suspended Solids
	150mg/l
	64
	SCA Blue Book 105
ISBN 011751957X
	30th November
	UKAS Lab 1314
	19.7%

	W2
	Total cadmium & its compounds
	0.005mg/l

(as annual average)
	0.0006
	BS EN ISO 5961:1995,

BS 6068-2.21:1995
	
	UKAS Lab 1314
	7.83%

	W2
	Total chromium & its compounds
	0.015mg/l

(as annual average)
	0.002
	BS EN ISO 11885:1998,

BS 6068-2.60:1998
	
	UKAS Lab 1314
	7.93%

	W2
	Total copper & its compounds
	0.01mg/l

(as annual average)
	0.009
	BS EN ISO 11885:1998,

BS 6068-2.60:1998
	
	UKAS Lab 1314
	9.03%

	W2
	Total mercury & its compounds
	0.0005mg/l

(as annual average)
	0.0001
	BS EN ISO 11885:1998,

BS 6068-2.60:1998
	
	UKAS Lab 1314
	11.5%

	W2
	Total nickel & its compounds
	0.03mg/l

(as annual average)
	0.004
	BS EN ISO 11885:1998,

BS 6068-2.60:1998
	
	UKAS Lab 1314
	8.82%

	W2
	Total zinc & its compounds
	0.07mg/l

(as annual average)
	0.052
	BS EN ISO 11885:1998,

BS 6068-2.60:1998
	
	UKAS Lab 1314
	9.85%

	W2
	Total arsenic & its compounds
	0.025mg/l

(as annual average)
	0.0018
	BS EN 26595:1993,

BS 6068-2.1:1983, ISO 6595-1985
	
	UKAS Lab 1314
	10.04%

	W2
	Total iron & its compounds
	None (mg/l)
	0.53
	SCA Blue Book 163

ISBN 0117532444
	
	UKAS Lab 1314
	9.27%

	W2
	Total cadmium & its compounds
	9150g
	302
	BS EN ISO 5961:1995,

BS 6068-2.21:1995
	
	UKAS Lab 1314
	7.83%

	W2
	Total mercury & its compounds
	915g
	126
	BS EN ISO 11885:1998,

BS 6068-2.60:1998
	
	UKAS Lab 1314
	11.5%


Form Number: W1

[1] The result given is the maximum value (or the minimum value in the case of a limit that is expressed as a minimum) obtained during the reporting period, expressed in the same terms as the emission limit value. Where the emission limit value is expressed as a range, the result is given as the ‘minimum – maximum’ measured values.

[2] Where an internationally recognised standard test method is used the reference number is given. Where another method that has been formally agreed with the Agency is used, then the appropriate identifier is given. In other cases the principal technique is stated, e.g. colorimetry.

[3] For non-continuous measurements the date and time of the sample that produced the result is given. For continuous measurements, or flow/time proportional samples, the percentage of the process operating time covered by the monitoring is given.   

[4] The accreditation status of the equipment and/or the monitoring organisation, as appropriate, for the methods used for both sampling and analysis.

[5] The uncertainty associated with the quoted result at the 95% confidence interval, unless otherwise stated. The following uncertainties are quoted on a different basis (basis as stated) – {The basis of any other uncertainty figure needs to be stated. Where no figure is available the Agency will need to agree an appropriate uncertainty value.} 

[6] The emission limit values for {pH} are expressed as {minimum and maximum individual values}.

Signed …………Kathryn Fowler………………………………………………….  

Date……24/1/2015…………………..




(authorised to sign as representative of the Operator)

Form Number: R1

Reporting of Waste Disposal and Recovery for the year Jan 1st 2014 to December 31st 2014
	Waste

Description
	Disposal
	Recovery
	
	Trends in Waste Disposal and Recovery

	
	Route
	Tonnes
	Tonnes
	
	Year
	Parameter

	
	
	
	
	
	
	Named 

Waste
	Total 

Waste
	Waste per unit output

	1) Hazardous Wastes
	
	
	
	
	2005
	33228
	33562
	Report on PI1

	Named haz. Waste
	Neales Waste Management
	42.58
	14.91
	
	2006
	12961
	12961
	Report on PI1

	Other hazardous wastes
	
	
	
	
	2007
	16383
	16383
	Report on PI1

	Total hazardous waste
	
	42.58
	14.91
	
	2008
	15801
	15801
	Report on PI1

	
	
	
	
	
	2009
	16623
	16623
	Report on PI1

	2) Non-Hazardous Wastes
	
	
	
	
	2010
	25378
	25378
	Report on PI1

	Named non-haz. Waste
	Neales Waste Mangement and n-virocycle
	20285
	20285
	
	2011
	32314
	32314
	Report on PI1

	Other non-hazardous wastes
	
	
	
	
	2012
	28122
	28122
	Report on PI1

	Total non-hazardous waste
	
	
	
	
	2013
	19823
	19823
	Report on PI1

	
	
	
	
	
	2014
	20327
	20327
	Report on PI1

	TOTAL WASTE
	
	20327
	20300
	
	
	
	
	


	Operator’s comments :

This waste is inclusive of sludge from our WWTP and onsite waste kiesulguhr tanks.  
This waste figure is also inclusive of all site projects (including CDM which are governed through waste management plans
Several initiatives have taken place this year, including asbestos removal in line with our asbestos management plan.  
5S activities are still on-going.
Zero to landfill initiative by Neale’s waste management, utilising refuse derived fuels (RDF)

Focus this coming year will be on the index of by products and waste (kg/NHl)



Signed …………………Kathryn Fowler………………………………………….  

Date……24/1/2015…………………..




(authorised to sign as representative of the Operator)

Form Number: WU1

Reporting of Water Usage for the year Jan 1st 2014 to December 31st 2014
	Water Source
	Usage

(m3)
	Specific Usage

(m3/t)
	
	Trends in Water Usage

	
	
	
	
	Year
	Parameter

	
	
	
	
	
	Spring Water Source
	Mains Water Source
	Total 

Water usage
	Water per unit output

	Spring water
	1721398
	3.90
	
	
	
	
	
	

	Mains water
	35496
	0.08
	
	2005
	2197934
	16813
	2214747
	Report on PI1

	
	
	
	
	2006
	2324340
	13139
	2337479
	Report on PI1

	
	
	
	
	2007
	2303437
	17217
	2320654
	Report on PI1

	
	
	
	
	2008
	2063466
	19462
	2082928
	Report on PI1

	TOTAL WATER USAGE
	1756894
	3.98
	
	2009
	1934551
	21173
	1955724
	Report on PI1

	
	
	
	
	2010
	2487347
	29020
	2516367
	Report on PI1

	
	
	
	
	2011
	1929724
	35197
	1964921
	Report on PI1

	
	
	
	
	2012
	1598898
	38003
	1636901
	Report on PI1

	
	
	
	
	2013
	1704598
	41397
	1745995
	Report on PI1

	
	
	
	
	2014
	1721398
	35496
	1756894
	Report on PI1


	Operator’s comments :

This is one of our Better World KPI’s, and is a huge focus of the business.  Our water KPI for 2015 is 3.5 hl/hl N.  
Several initiatives and CAPEX have been identified to further reduce water usage in a sustainable manner, whilst maintaining the quality of our brands.


Signed ……………………Kathryn Fowler……………………………………….  

Date………24/1/2015………………..




(authorised to sign as representative of the Operator)

Form Number: E1

Reporting of Energy Usage for the year Jan 1st 2014 to December 31st 2014
	Energy Source
	Energy Usage
	CO2
Produced

(tonnes)
	
	Trends in Energy Usage

	
	Quantity
	Primary Energy

(MWh)
	
	
	Year
	Parameter

	
	
	
	
	
	
	Primary Energy usage
	CO2

produced
	CO2 per unit output

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	2005
	229412
	43030
	Report on PI1

	Electricity *
	37942
	91061
	15025
	
	2006
	227217
	42470
	Report on PI1

	Natural Gas
	96320
	96320
	18301
	
	2007
	234066
	43253
	Report on PI1

	Gas Oil
	301707
	3171
	793
	
	2008
	218651
	40094
	Report on PI1

	
	
	
	
	
	2009
	206460
	38506
	Report on PI1

	
	
	
	
	
	2010
	222367
	42261
	Report on PI1

	TOTAL
	435969
	190552
	34119
	
	2011
	214616
	39697
	Report on PI1

	
	
	
	
	
	2012
	198037
	35880
	Report on PI1

	
	
	
	
	
	2013
	185342
	33131
	Report on PI1

	
	
	
	
	
	2014
	190552
	34119
	


* Conversion factor for delivered electricity to primary energy = 2.4
	Operator’s comments :

The site is heavily focussed on better world targets including electricity and heat.  Site KPI’s have been significantly reduced (10%) for 2014. 
2015 Capex projects will be highlighted in the EMS document



Signed ………Kathryn Fowler…………………………………………………….  

Date……24/1/2015…………………..




(authorised to sign as representative of the Operator)

Form Number: PI1

Reporting of Performance Indicators for the year Jan 1st 2014 to December 31st 2014
	Annual Production/Treatment

	Production of beers and lagers
	441931 tonnes


Environmental Performance Indicators

	Parameter
	Annual Average
	Units
	
	Trends in Environmental Performance

	
	
	
	
	Year
	Parameter
	
	
	
	
	

	
	
	
	
	
	BOD
	COD
	Water Use
	Energy Use
	CO2
	Waste

	BOD
	0.0172
	kg/tonne
	
	
	kg/tonne
	kg/tonne
	m3/tonne
	kWh/tonne
	tonne/tonne
	tonne/tonne

	COD
	0.172
	kg/tonne
	
	2005
	0.104
	0.450
	4.86
	504
	0.020*
	0.074

	Water use
	3.69
	m3/tonne
	
	2006
	0.021
	0.256
	5.31
	516
	0.021*
	0.029

	Energy use
	431
	kWh/tonne
	
	2007
	0.034
	0.306
	5.90
	600
	0.024
	0.042

	Carbon dioxide
	0.08
	tonne/tonne
	
	2008
	0.058
	0.378
	5.67
	596
	0.019
	0.043

	Waste
	0.046
	tonne/tonne
	
	2009
	0.06
	0.27
	4.63
	489
	0.020
	0.039

	
	
	
	
	2010
	0.08
	0.33
	5.58
	493
	0.095
	0.056

	
	
	
	
	2011
	0.043
	0.27
	4.57
	499
	0.092
	0.069

	
	
	
	
	2012
	0.029
	0.22
	4.07
	508
	0.092
	0.070

	
	
	
	
	2013
	0.020
	0.162
	4.31
	457
	0.08
	0.050

	
	
	
	
	2014
	0.0172
	0.172
	3.69
	431
	0.08
	0.046


	Operator’s comments :

Waste management has improved, despite numerous site based projects this year. Data collection for all waste streams has also improved significantly.  These figures include all waste exiting the site (both dry and wet).  Further initiatives through our incumbent supplier include further segregation at a MRF, and the use of refuse derived fuels.  Projects for this year include de-watering of sludge for 2015.
Focus for 2014 will include 10% reduction in C02 emissions and energy usage, by the continued use of Capital investment and Energy Guardian Initiatives.




Signed ………………Kathryn Fowler…………………………………………….  

Date……24/1/2015…………………..




(authorised to sign as representative of the Operator)

Form Number: MR1

Reporting of Mass Release for the year Jan 1st 2014 to December 31st 2014.

	Mass Release 
	
	Trends in Mass Release

	Parameter
	kg/annum
	
	
	
	

	
	
	
	Year
	Parameter
	

	
	
	
	
	
	Ammonia (kg/annum)
	

	Ammonia (refrigerant)
	
	0
	
	2005
	1000
	

	
	
	
	
	2006
	4000
	

	
	
	
	
	2007
	1000
	

	
	
	
	
	2008
	1000
	

	
	
	
	
	2009
	1000
	

	
	
	
	
	2010
	1000
	

	
	
	
	
	2011
	0
	

	
	
	
	
	2012
	1060
	

	
	
	
	
	2013
	0
	

	
	
	
	
	2014
	0
	


	Operator’s comments :




Signed ……………Kathryn Fowler……………………………………………….  

Date………24/1/2015………………..



(authorised to sign as representative of the Operator)

Permit Reference Number: AannnnAA

Date of Form: dd/mm/yy

Permit Reference Number: BX7282IS

Date of Form: 01/06/05

