Permit Reference Number:

Installation:

Operator:
Permit Reference Number: BX72821S

Installation: InBev Magor Brewery

Operator: InBev UK Ltd

Form Number : W1

Reporting of Emissions to Water (other than to Sewer) for the period from 1st January to 31st March 2018
	Emission

Point
	Substance /

Parameter
	Emission

Limit Value
	Result [1]
	Test

Method [2]
	Sample

Date and Times [3]
	Accreditation/

Certification [4]
	Uncertainty

[5]

	W2
	Flow
	10,000m3/day
	7045
	Continuous / cumulative – AAB flow meter
	10th March 2018
	MCerts accredited
	+/- 1.04 %

	W2
	Flow
	126 litres/s
	61.38
	Spot – AAB flow meter
	10th March 2018
	MCerts accredited
	+/- 1.04 %

	W2
	pH
	5 – 9 [6]
	Min – 6.9
Max – 8.8
	Continuous sample 
	3rd January 2018
1st & 2nd January 2018
	EA approved (IP 18)
	+/- 0.05 pH

	W2
	Temperature
	30°C
	21.4
	Continuous sample – knick in line meter
	10th March 2018
	EA approved (IP 18)
	+/- 1 degree C

	W2
	BOD
	200mg/l
	26
	SCA Blue Book 130
ISBN 0117522120
	18th March 2018
	UKAS Lab 1314
	20.1%

	W2
	COD
	450mg/l
	151
	SCA Blue Book 97
ISBN 0117519154
	16th January 2018
	UKAS Lab 1314
	5.8%

	W2
	Suspended Solids
	150mg/l
	115
	SCA Blue Book 105
ISBN 011751957X
	15th January 2018
	UKAS Lab 1314
	19.7%

	W2
	Total cadmium & its compounds
	0.005mg/l

(as annual average)
	
	
	
	
	

	W2
	Total chromium & its compounds
	0.015mg/l

(as annual average)
	
	
	
	
	

	W2
	Total copper & its compounds
	0.01mg/l

(as annual average)
	
	
	
	
	

	W2
	Total mercury & its compounds
	0.0005mg/l

(as annual average)
	
	
	
	
	

	W2
	Total nickel & its compounds
	0.03mg/l

(as annual average)
	
	
	
	
	

	W2
	Total zinc & its compounds
	0.07mg/l

(as annual average)
	
	
	
	
	

	W2
	Total arsenic & its compounds
	0.025mg/l

(as annual average)
	
	
	
	
	

	W2
	Total iron & its compounds
	None
	
	
	
	
	

	W2
	Total cadmium & its compounds
	9150g
	
	
	
	
	

	W2
	Total mercury & its compounds
	915g
	
	
	
	
	


Form Number : W1

[1] The result given is the maximum value (or the minimum value in the case of a limit that is expressed as a minimum) obtained during the reporting period, expressed in the same terms as the emission limit value. Where the emission limit value is expressed as a range, the result is given as the ‘minimum – maximum’ measured values.

[2] Where an internationally recognised standard test method is used the reference number is given. Where another method that has been formally agreed with the Agency is used, then the appropriate identifier is given. In other cases the principal technique is stated, e.g. colorimetry.

[3] For non-continuous measurements the date and time of the sample that produced the result is given. For continuous measurements, or flow/time proportional samples, the percentage of the process operating time covered by the monitoring is given.   

[4] The accreditation status of the equipment and/or the monitoring organisation, as appropriate, for the methods used for both sampling and analysis.

[5] The uncertainty associated with the quoted result at the 95% confidence interval, unless otherwise stated. The following uncertainties are quoted on a different basis (basis as stated) – {The basis of any other uncertainty figure needs to be stated. Where no figure is available the Agency will need to agree an appropriate uncertainty value.} 

[6] The emission limit values for {pH} are expressed as {minimum and maximum individual values}.

Signed ……Carl Rogers……………………………………………………….  

Date………26/04/18

(authorised to sign as representative of the Operator)

Permit Reference Number: AannnnAA

Date of Form: dd/mm/yy

Permit Reference Number: BX7282IS

Date of Form: 01/06/05

