Schedule 6 – Notification 

Schedule 6 – Notification 


These pages outline the information that the operator must provide.

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission.  Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

If any information is considered commercially confidential, it should be separated from non-commercial information, supplied on a separate sheet and accompanies by an application for commercial confidentiality under the provision of the PPC Regulations.

Part A

	Permit Number
	FP3238SL

	Name of Operator
	Novera Energy No 2 Ltd

	Location of Installation
	Lamby Way Generation Plant

	Time and date of the detection
	14/09/15


	(a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques, accident, or fugitive emission which has caused, is causing or may cause significant pollution

	To be notified within 24 hours of detection

	Time and date of the event
	

	Reference or description of the location of the event
	

	Description of where any release into the environment took place
	

	Substance(s) potentially released
	

	Best estimate of the quantity or rate of release of substances
	

	Measures taken or intended to be taken, to stop the emission 
	

	Description of the failure or accident
	


	(b) notification requirements for the breach of a limit

	To be notified within 24 hours of detection unless otherwise specified below

	Emission point reference / source
	Flare #1

	Parameter(s)
	CO and VOC

	Limit
	CO: 50 mg/m3   VOC: 10mg/m3

	Measured value and uncertainty
	CO: 311mg/m3 (4.5% measurement uncertainty)
VOC: 31mg/m3 (9.7% measurement uncertainty)

	Date and time of monitoring
	03/09/15  11:45 – 12:45

	Measures taken, or intended to be taken, to stop the emission
	Flare #1 has been turned off. Flare #2 will be used as necessary until the cause of the excessive emissions has been investigated and resolved.

	Time periods for notification following detection of a breach of a limit

	Parameter
	Notification period

	
	

	
	

	
	


	(c) Notification requirements for the detection of any significant adverse environmental effect

	To be notified within 24 hours of detection

	Description of where the effect on the environment was detected
	

	Substance(s) detected
	

	Concentrations of substances detected
	

	Date of monitoring/sampling
	


Part B – to be submitted as soon as practicable
	Any more accurate information on the matters for notification under Part A
	

	Measures taken, or intended to be taken, to prevent a recurrence of the incident
	

	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission
	

	The dates of any unauthorised emissions from the installation in the preceding 24 months
	


	Name*
	Richard Clarke

	Post
	Technician, Compliance & services

	Signature
	

	Date
	14/09/15


*authorised to sign on behalf of Novera Energy 

