Notification of a Release Exceeding Consent Limit

Part A

	Permit Number
	UP3836SS

	Name of Operator
	Zeon Chemicals Europe Ltd

	Location of Installation
	Sully Moors Road, Sully, Vale of Glamorgan

	Time & Date of the detection
	Q2 2014


	(a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques, accident, or fugitive emission which has caused, is causing or may cause significant pollution.

	To be notified within 24 hours of detection

	Date & time of the event
	

	Reference or description of the location of the event
	

	Description of where any release into the environment took place
	

	Substance(s) potentially released
	

	Best estimate of the quantity or rate of release of the substances
	

	Measures taken, or intended to be taken, to stop any emission.
	

	Description of the failure or accident
	


	(b) Notification requirements for the breach of a limit

	To be notified within 24 hours of detection unless otherwise specified below

	Emission point reference / source
	A6

	Parameter(s)
	Acrylonitrile to air

	Limit
	A6 = 0.1 kg/hr.

	Measured value & uncertainty
	A6 = 0.14kg/hr. (+/- 20%)

	Date & time of monitoring
	A6 Maximum recorded 19/5/2014


	Measures taken, or intended to be taken, to stop any emission.
	Investigations ongoing into cause of exceedance. No clear indication for the exceedance at this stage, since residual AN levels on intermediate products are good.


	Time periods for notification following detection of a breach of a limit

	Parameter
	Notification Period

	
	

	
	

	
	


	(c) Notification requirements for the detection of any significant adverse environmental effect

	To be notified within 24 hours of detection

	Description of where the effect on the environment was detected
	

	Substance(s) detected
	

	Concentrations of substances detected
	

	Date of monitoring / sampling
	


Part B

	Any more accurate information on the matters for notification under Part A
	 

	Measures taken, or intended to be taken, to prevent a recurrence of the incident
	

	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission
	

	The dates of any unauthorised emissions from the installation in the preceding 24 months
	


	Name*
	Martin Davies

	Post
	HSE Manager

	Signature
	

	Date
	16/7/2014


* Authorised to sign on behalf of Zeon Chemicals Europe Ltd.
