Schedule 6 – Notification 

These pages outline the information that the Operator must provide.

Units of measurements used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission.  Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the PPC Regulations.

	Part A
	
	
	
	
	

	
	
	
	
	
	

	Permit Number
	ZP3535SQ

	Name of Operator
	Novera Energy Generation 2 Ltd (Infinis Plc)

	Location of the Installation
	Silent Valley gas utilisation plant

	Time and date of the detection
	29/06/15  18:06

	
	
	
	
	
	

	(a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques, accident , or fugitive emission which has caused, is causing or may cause, significant pollution

	
To be notified within 24 hours of detection

 

	Date and time of the event
	28/06/15 01:17 – 29/06/15 13:13

	Reference or description of the location of the event
	GUP 

	Description of where any release into the environment took place
	Silent Valley landfill

	Substance(s) potentially released
	Landfill gas (potentially)

	Best estimate of the quantity or the rate of release of substances
	Unquantifiable 

	Measures taken, or intended to be taken, to stop any emission
	Technician attended site and restarted the gas plant

	Description of the failure or accident.
	Gas abstraction system interruption due to engine and flare faults

	
	
	
	
	
	

	(b) Notification requirements for the breach of a limit

	
To be notified within 24 hours of detection unless otherwise specified below
 

	Emission point/reference source
	

	Parameter(s)
	

	Limit
	

	Measured value and uncertainty
	

	Date and time of monitoring
	 

 

 

	Measures taken, or intended to be taken to stop the emission
	


	
	
	
	
	
	

	
Time periods for notification following detection of a breach of a limit

 

	Parameter
	Notification period

	
	

	
	

	
	

	
	
	
	
	
	

	(c) Notification requirements  for the detection of any significant adverse environmental effect

	
To be notified within 24 hours of detection



	Description of where the effect on the environment was detected
	

	Substance(s) detected
	

	Concentrations of substances detected
	

	Date of monitoring/sampling
	 

 

 


Part B – to be submitted as soon as practicable
	Any more accurate information on the matters for notification under Part A
	

	Measures taken, or intended to be taken, to prevent recurrence of the incident
	

	Measures taken, or intended to be taken to rectify, limit of prevent any pollution of the environment which has been or may be caused by the emission
	

	The dates of any unauthorised emissions from the installation in the preceding 24 months
	


	Name*
	Richard Clarke

	Post
	Technician, Compliance

	Signature
	[image: image1.emf]

	Date
	30/06/15

	*authorised to sign on behalf of Infinis
	


