Permit Number: EPR/SP3537VQ





Operator: Biogen (UK) Ltd
Facility: Biogen Bryn Pica







Form Number: Air1 16/01/14
Reporting of emissions to air for the period from 01/01/2015 to 30/04/2016 
	Emission

Point
	Substance /

Parameter
	Emission

Limit Value
	Reference Period
	Result [1]
	Test

Method [2]
	Sample

Date and Times [3]
	Uncertainty

[4]

	A1 CHP Exhaust
	Oxides of Nitrogen
	500 mg/m3
	Hourly mean
	385
	BS EN 14792
	27/04/16
	±20

	A1 CHP Exhaust
	Carbon Monoxide
	1400 mg/m3
	Hourly mean
	838
	BS EN 15058
	27/04/16
	±45

	A1 CHP Exhaust
	Sulphur Dioxide
	350 mg/m3
	Hourly mean
	447
	BS EN 14791
	27/04/16
	±29

	A1 CHP Exhaust
	VOCs
	1000 mg/m3
	Hourly mean
	620
	 BS EN 12619:1999 or 13526:2002 depending on concentration
	27/04/16
	±29


The result given is the maximum value (or the minimum value in the case of a limit that is expressed as a minimum) obtained during the reporting period, expressed in the same terms as the emission limit value. Where the emission limit value is expressed as a range, the result is given as the ‘minimum – maximum’ measured values.

Where an internationally recognised standard test method is used the reference number is given. Where another method that has been formally agreed with Natural Resources Wales is used, then the appropriate identifier is given. In other cases the principal technique is stated, for example gas chromatography.

For non-continuous measurements the date and time of the sample that produced the result is given. For continuous measurements the percentage of the process operating time covered by the result is given.   The uncertainty associated with the quoted result at the 95% confidence interval, unless otherwise stated.
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	Operator’s comments :
The attached results are as per Emissions Report R16108 submitted together with this report.



Signed: Esther Hombarume (Environment Manager)                                                                                                                                  Date: 23/05/2016   



(Authorised to sign as representative of Operator)

