Schedule 5 – Notification


PART A

	Permit Number
	EPR/SP3537VQ

	Name of Operator
	Biogen Bryn Pica Limited

	Location of Facility
	Merthyr Road, Llwycoed, Aberdare, Mid Glamorgan, CF44 0BX

	Time and date of the detection
	23/05/16 10:15am


	(a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques, accident, or fugitive emission which  has caused, is causing or may cause significant pollution

	To be notified within 24 hours of detection

	Date and time of the event
	

	Reference or description of the location of the event
	

	Description of where any release into the environment took place
	

	Substance(s) potentially released
	

	Best estimate of the quantity or rate of release of substances
	

	Measures taken, or intended to be taken, to stop any emission
	

	Description of the failure or accident
	


	(b) Notification requirement for the breach of a limit

	To be notified within 24 hours of detection unless otherwise specified below

	Emission point reference/source
	CHP exhaust

	Parameter(s)
	SO2

	Limit
	350mg/m3

	Measured value and uncertainty
	447 mg/m3  (±29 mg/m3)

	Date and time of monitoring
	27/04/16  11:45 – 12:45

	Measures taken, or intended to be taken, to stop the emission
	An automated ferric chloride dosing system is in place and weekly monitoring of H₂S in biogas using RAE tubes is carried out. A retest following the review and verification of the dosing rates to be undertaken. Routine servicing and maintenance of the CHP to continue.


	Time periods for notification following detection of a breach of a limit

	Parameter
	Notification period

	
	

	
	

	
	


	(c) Notification requirements for the detection of  any significant adverse environmental effect

	To be notified within 24 hours of detection

	Description of where the effect on the environment was detected
	

	Substance(s) detected
	

	Concentrations of substances detected
	

	Date of monitoring/sampling
	


PART B – TO BE SUBMITTED AS SOON AS PRACTICABLE
	Any more accurate information on the matter for notification under Part A
	

	Measures taken,  intended to be taken, to prevent a reoccurrence of the incident
	

	Measures taken or intended to be taken to rectify, limit, or prevent  any pollution of the environment which has been or may be caused by the emission
	

	The dates of any unauthorised emissions from the facility in the preceding 24 months
	


	Name*
	Esther Hombarume

	Post
	Environment Manager

	Signature
	E. Hombarume

	Date
	23/05/16


*Authorised to sign on behalf of Biogen (UK) limited
