Permit Number: 
VP3132LJ





Operator: 

Maxibrite Limited

Installation:

Mwyndy Solid Fuel Briquette Manufacturer

Form Number: 
Water1 / 15/06/07
Reporting of emissions to water (other than to sewer) for the period from    01/07/2015 to 30/09/2015
	Emission

Point
	Substance /

Parameter
	Emission

Limit Value
	Reference Period
	Test

Method [2]
	Result [1]
	Sample

Date and Times [3]
	Uncertainty

[4]
	Weather 

Conditions



	W1 on site plan in schedule 2
	Temperature
	28°C
	Spot sample
	TK digital thermometer, with K-type connection.
	24.2
	01/07 @ 1130
	
	Dry

	
	
	
	
	
	21.4
	08/07 @ 1700
	
	Dry

	
	
	
	
	
	20.3
	13/07 @ 0730
	
	Rain

	
	
	
	
	
	19.0
	22/07 @ 1100
	
	Showers

	
	
	
	
	
	18.6
	27/07 @ 0845

29/07 @ 1830
	
	Rain
Dry

	
	
	
	
	
	20.8
	03/08 @ 0700
	
	Dry

	
	
	
	
	
	19.5
	12/08 @ 1825
	
	Dry

	
	
	
	
	
	21.9
	18/08 @ 2130
	
	Dry

	
	
	
	
	
	19.2 
	24/08 @ 1345
	
	Rain

	
	
	
	
	
	18.2
	02/09 @ 1830
	
	Dry

	
	
	
	
	
	20.0
	11/09 @ 1145
	
	Dry

	
	
	
	
	
	17.4
	15/09 @ 0905
	
	Dry

	
	
	
	
	
	17.4
	21/09 @ 2300
	
	Rain

	
	
	
	
	
	17.7
	28/09 @ 2245
	
	Dry

	W1 on site plan in schedule 2
	pH
	6-9
	Spot sample
	WTW 315i digital pH meter with Sentix 41 gel filled electrode, method based on SCA blue book 14 (method approved and accepted by EA).
	7.81 – 8.04
	7.81 02/07 @ 2200 8.04 01/07 @ 1130
	
	Dry
Dry

	
	
	
	
	
	7.91 – 8.03
	7.91 06/07 @ 1200 8.03 08/07 @ 1700
	
	Dry

Dry

	
	
	
	
	
	7.67 – 8.21
	7.67 13/07 @ 0730 8.21 17/07 @ 0840
	
	Rain
Dry

	
	
	
	
	
	7.72 – 8.53
	7.72 24/07 @ 0630 8.53 26/07 @ 1030
	
	Rain
Light Rain

	
	
	
	
	
	8.26 – 8.47
	8.26 29/07 @ 1830 8.47 27/07 @ 0845
	
	Dry
Rain

	
	
	
	
	
	8.37 – 8.39
	8.37 05/08 @ 0910 8.39 03/08 @ 0700
	
	Dry

Dry

	
	
	
	
	
	8.16 – 8.22
	8.16 13/08 @ 1820 8.22 12/08 @ 1825
	
	Dry

Dry

	
	
	
	
	
	7.59 – 8.42
	7.59 17/08 @ 2235 8.42 19/08 @ 1915
	
	Dry

Rain

	
	
	
	
	
	8.14 – 8.83
	8.14 28/08 @ 1000 8.83 26/08 @ 0640
	
	Dry
L. Showers

	
	
	
	
	
	8.18 – 8.26
	8.18 02/09 @ 1830
8.26 01/09 @ 1100
	
	Dry
Dry

	
	
	
	
	
	7.82 – 8.19
	7.82 08/09 @ 1845 8.19 11/09 @ 1145
	
	Dry

Dry

	
	
	
	
	
	8.05 – 8.17
	8.05 18/09 @ 1355 8.17 14/09 @ 0850
	
	Dry

L. Showers

	
	
	
	
	
	8.06 – 8.24
	8.06 21/09 @ 0820 8.24 23/09 @ 2300
	
	Rain
Light rain

	
	
	
	
	
	7.51 – 8.31
	7.51 29/09 @ 1910 8.31 30/09 @ 0900
	
	Dry

Dry

	W1 on site plan in schedule 2
	Ammonia (total as N)
	7mg/l
	Spot sample
	ISO 7150-2 UKAS Accredited Laboratory/MCERTS (ALcontrol)
	2.05
	17/07 @ 0840
	
	Dry

	
	
	
	
	
	2.57
	25/08
	
	Dry

	
	
	
	
	
	2
	30/09 @ 0900
	
	Dry

	W1 on site plan in schedule 2
	Total suspended solids
	200 mg/l
	Spot sample
	BS EN872 UKAS Accredited Laboratory/MCERTS (ALcontrol )
	30
	17/07 @ 0840
	
	Dry

	
	
	
	
	
	7.5
	25/08
	
	Dry

	
	
	
	
	
	2.5
	30/09 @ 0900
	
	Dry


1. The result given is the maximum value (or the minimum value in the case of a limit that is expressed as a minimum) obtained during the reporting period, expressed in the same terms as the emission limit value. Where the emission limit value is expressed as a range, the result is given as the ‘minimum – maximum’ measured values.

2. Where an internationally recognised standard test method is used the reference number is given. Where another method that has been formally agreed with the Agency is used, then the appropriate identifier is given. In other cases the principal technique is stated, e.g. gas chromatography.

3. For non-continuous measurements the date and time of the sample that produced the result is given. For continuous measurements the percentage of the process operating time covered by the result is given.   

4. The uncertainty associated with the quoted result at the 95% confidence interval, unless otherwise stated.

Signed ……………………John Keenan……………………………………….  

Date…………30/09/2015…………..   



(Authorised to sign as representative of Operator)

