Schedule 5 - Notification 

These pages outline the information that the operator must provide. 

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.

Part A 

	Permit Number
	EPR/LP3030XA

	Name of operator
	Viridor Waste Management Limited

	Location of Facility
	Cardiff Energy from Waste Facility, Trident Park, Cardiff.

	Time and date of the detection 
	19_12_2017 at 00:26H


	(a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques, accident, or fugitive emission which has caused, is causing or may cause significant pollution

	To be notified within 24 hours of detection

	Date and time of the event
	

	Reference or description of the location of the event 
	

	Description of where any release into the environment took place
	

	Substances(s) potentially released
	

	Best estimate of the quantity or rate of  release of substances
	

	Measures taken, or intended to be taken, to stop any emission
	

	Description of the failure or accident.
	


	(b) Notification requirements for the breach of a limit

	To be notified within 24 hours of detection unless otherwise specified below

	Emission point reference/ source
	A2

	Parameter(s)
	HCl

	Limit
	Daily mean limit                10mg/m3                             

½ hour mean limit            60mg/m3


	Measured value and uncertainty
	Daily mean recorded at 10.94mg/m3                              

½ hour mean recorded at 65.18mg/m3 for the 30 minutes between 22:30H and 22:59H.


	Date and time of monitoring
	18 December 2017,
(i) Daily mean monitored throughout that day with results becoming available within 60 minutes of the end of the day.

(ii) ½ hour mean results become available at the end of that sample ½ hour.


	Measures taken, or intended to be taken, to stop the emission
	(i) Review quantity of waste plastic being accepted at site. 

(ii) Vigilant review of emissions throughout the day.


	Time periods for notification following detection of a breach of a limit

	Parameter
	Notification period

	
	

	
	

	
	


	(c) Notification requirements for the detection of any significant adverse environmental effect

	To be notified within 24 hours of detection

	Description of where the effect on the environment was detected
	

	Substances(s) detected
	

	Concentrations of substances detected
	

	Date of monitoring/sampling
	


Part B - to be submitted as soon as practicable

	Any more accurate information on the matters for notification under Part A.
	A full review of data has now been undertaken and indicates that the HCl spike only occurred between 22:30 and 23:00H. The Control Room undertook the correct steps to retrieve the situation by reducing waste throughput and increasing lime dosage. However, due to the lateness in the day when the HCl spike occurred the daily mean ELV was exceeded as this value is calculated from midnight to midnight.

 

	Measures taken, or intended to be taken, to prevent a recurrence of the incident
	The control room have been reminded that the waste being placed on the grate should be of a homogeneous composition. 


	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission
	As above.

	The dates of any unauthorised emissions from the facility in the preceding 24 months.
	23/05/2016 

09/09/2016 

11/09/2016 

11/09/2016 

22/09/2016 

22/02/2017 

17/04/2017 

22/04/2017 

24/04/2017 

02/05/2017  

30/05/2017  

01/06/2017 
06/06/2017  
09/06/2017  

18/06/2017 

19/06/2017 

29/06/2017 

04/07/2017 
21/07/2017 
24/07/2017 
28/07/2017 
31/07/2017 



Part C

	Permit Number
	EPR/LP3030XA

	Name of operator
	Viridor Waste Management Limited

	Location of installation
	Cardiff Energy from Waste Facility, Trident Park, Cardiff.


	Time at which abnormal operation commenced
	

	Time at which abnormal operation ceased
	

	Duration of this incidence of abnormal operation
	

	Cumulative abnormal operation duration in current year (at end of present incidence)
	

	Reasons for abnormal operation
	

	How did the abnormal operation end? (e.g. plant repaired, reaching maximum permitted duration, initiation of shutdown, etc.)
	

	Where the abnormal operation was caused by the failure of the particulate, CO or TOC CEM, attach a copy of the alternate monitoring data which was used to demonstrate compliance with the abnormal operation emission limit values.
	

	Where abatement plant has failed, give the half-hourly average emissions for pollutants of relevance during the abnormal operation in the rows below

	Pollutant
	1st ½ hour
	2nd ½ hour
	3rd ½ hour
	4th ½ hour
	5th ½ hour
	6th ½ hour
	7th ½ hour
	8th ½ hour

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	
	
	
	
	
	
	
	
	

	Name*
	Gwyn Jones 

	Post
	Environment, Health and Safety Manager 

	Signature
	G Jones 

	Date
	09_01_2018


* authorised to sign on behalf of Viridor Waste Management Limited
