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Schedule 1

Notification of Unauthorised Release

Operator:

Tata Steel UK Ltd


Authorisation:
BS3905

Location:

Llanwern Works











Newport


Date Submitted:






South Wales











NP19 4QZ

	PART B

	· Further details of the release and results of any investigations carried out
This Part B is a follow-up to the Part A Notification (submitted on the 19/11/15) related to

elevated Suspended Solids emissions at the W1 effluent consent point.

A peak concentration of 548 mg/l was observed, and as per similar breaches of this kind – it

is considered to be as a result of rainfall, and the associated increase in solids from off-site

sources. The daily suspended solids samples taken at Drain 9 (just downstream from one of

the main influents) showed an average Suspended Solids concentration from the preceding few days to be 1732 mg/l i.e. well in excess of the 100 mg/l W1 consent limit. It would seem that the effluent drainage lagoon system which serves to drop-out such solids, had not been able to cope with the increase contribution from off-site sources

	· Measures taken or intended to be taken to prevent a recurrence of the incident
No additional measures are proposed currently

	· Measures taken, or intended to be taken, to: rectify, limit or prevent any pollution of the environment or harm which has been caused by the emission

None Proposed

	· The dates of any PART A notifications within the previous 24 months

Breach of HCl to Atmosphere consent limit at Pickle Line No 2

· 01/07/14

· 08/10/15

Breach of Suspended Solids W1 consent point.

· 24/09/15
Monitoring Data not reported (Lab equipment failure)

· 23/02/14


Name: Jason Heatman

Position:  Lead Environmental Engineer
Signature:
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Signed on behalf of Tata Steel Strip Products UK][
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