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Schedule 1
Notification of Unauthorised Release
Operator: 

Tata Steel Strip Products UK
Authorisation:

BS3905

Location: 
Llanwern works









Newport 
Date Submitted:
24.08.2016



South Wales









NP19 4QZ
	

PART A

	· Name of the prescribed substance or other substance which might cause harm
Suspended solids in effluent

	· Time, date and location of the release
Elevated suspended solids were observed on 21st  August 2016 at the W1 effluent release  point

	· Best estimate of the quantity of the substance released, or the rate of release and the time during which the release took placed
Concentration levels in excess of the 100mg/l limit were recorded with a peak of 654 mg/l 


	· Additional information
An investigation took place on 24th August and a revised sampling technique is being proposed to reduce the possibility of disturbance of the sludge bed increasing solids in the sample. In addition it is proposed to dredge the lagoon to remove the sludge layer next week to reduce the possibility of solids carry over from the lagoon itself. With these measures implemented, it will reduce the likelihood of elevated solids during dry conditions.

	· Measures taken, or intended to be taken to stop the release
Investigating drain outlets that could influence this release.


Name:
Jason Heatman



Position:  Lead environmental Engineer
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