Part A 
	Permit Number
	RP3133LD

	Name of operator
	RWE Generation UK plc

	Location of Installation
	ABERTHAW POWER STATION

	Time and date of the detection 
	28th July 2015


	(a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques, accident, or fugitive emission which has caused, is causing or may cause significant pollution

	To be notified within 24 hours of detection

	Date and time of the event
	

	Reference or description of the location of the event 
	

	Description of where any release into the environment took place
	

	Substances(s) potentially released
	

	Best estimate of the quantity or rate of  release of substances
	

	Measures taken, or intended to be taken, to stop any emission
	

	Description of the failure or accident.
	


	(b) Notification requirements for the breach of a limit

	To be notified within 24 hours of detection unless otherwise specified below

	Emission point reference/ source
	W2 

	Parameter(s)
	pH

	Limit
	5.8 minimum 6-8.5 95%ile of instantaneous measurements

	Measured value and uncertainty
	2.3 pH Units
Uncertainty +/-0.1 pH Units

	Date and time of monitoring
	Main Troll 1 continuous pH monitoring probe in seal pit before outfall towers. On the 14/06/15 the pH dropped below 6 at 13:24 to 2.3 at 13:43 and returned to 6 at 14:18.  Backup Troll 2 showed similar readings.  



	Measures taken, or intended to be taken, to stop the emission
	The pH fell below the permit limit for a period of approximately 54 minutes. At the time of the event the CW system was not operational, this combined with the incoming tide may have meant that the low pH effluent would not have travelled down the outfall discharge structures and discharged from site. An investigation will be undertaken.      


	Time periods for notification following detection of a breach of a limit

	Parameter
	Notification period

	
	

	
	

	
	


	(c) Notification requirements for the detection of any significant adverse environmental effect

	To be notified within 24 hours of detection

	Description of where the effect on the environment was detected
	

	Substances(s) detected
	

	Concentrations of substances detected
	

	Date of monitoring/sampling
	


Part B - to be submitted as soon as practicable
	Any more accurate information on the matters for notification under Part A.
	

	Measures taken, or intended to be taken, to prevent a recurrence of the incident
	

	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission
	

	The dates of any unauthorised emissions from the installation in the preceding 24 months.
	


	Name*
	Amy Lavisher

	Post
	Environmental Compliance Engineer

	Signature
	

	Date
	30/07/15


* authorised to sign on behalf of RWE npower plc.

