For external use

This is a formal consultation form to be used when Natural Resources Wales needs to consult with the local Fire and Rescue Service (FRS) regarding a Fire Prevention and Mitigation Plan (FPMP) for an application for a new bespoke permit/ variation application or an existing permitted waste site.

The FPMP should be assessed using the current NRW Fire Prevention & Mitigation Plan guidance - waste management, which has been badged by the three fire services in Wales.

The relevant FRS contact email addresses to send a copy of this form to can be found at the end of this form. Each FRS have agreed to return any comments within 20 working days.

Comments from the FRS are welcome on all aspects of the FPMP, in particular – - Water supplies - Managing waste stack sizes and separation distances - Fire suppression systems - Fire fighting - Fire Detection and Managing Water Run-off - Any other specific aspects highlighted by the NRW officer requesting consultation comments.

Comments are welcome on this form.

PLEASE COMPLETE THE FOLLOWING INFORMATION

| FPMP consultation comments – site name and address |  |
| --- | --- |
| Name and job title of NRW officer | Kirsty Thomas – Senior Permitting Officer Installations and RSR Permitting |
| Email address | Kirsty.Thomas@cyfoethnatureiolcymru.gov.uk |
| Directorate – Operations or Permitting | Permitting |
| Applicant name / Operator name | Biffa Waste Services Limited |
| Site name and address | Cardiff Waste Management Resource Centre, Waterside Business Park, Lamby way, Rumney, Cardiff, CF3 2EQ |
| Application reference number / EPR reference number | PAN-010745 |
| Purpose of FPMP | New bespoke application |
| FRS consulted – i.e. NWFRS, SWFRS, Mid & West FRS | SWFRS |
| Date consultation sent - | 08/12/2020 |
| Date consultation due by – (20 working days – add date) | 07/01/2021 |
| Name and job title of FRS officer completing form | Stuart Brock |
| Email address | s-brock@southwales-fire.gov.uk |
| Date consultation made | 18/12/2020 |

Fire & Rescue Service comments on FPMP:

Please see my findings so far. Confirmation required from Dwr Cymru as to flowrates and pressure provided by identified hydrant. Confirmation also required that hydrant is suitable and sufficient. i.e accessible and maintained. Confirmation required for firefighting strategy out of operational hours. There is mention that there are contact details in the Incident response plan. Will machine operatives be available out of operational hours? With reference to the appendices, there appears to be conflicting information in the appendices that do not match the site, and subsequently don’t match the FPMP. Could you have a look and provide information only for the intended site and FPMP please? Ie is this the site plan for the intended site? I cannot see the hydrant on the plan in the location that the FPMP identifies. There does not appear to be the same number of bays as detailed in the FPMP etc If you could have a look and get back to me with your findings that would be most appreciated.

| Fire and Rescue Service email addresses for FPMP consultations |  |
| --- | --- |
| North Wales FRS |  |
| Gwynedd / Mon | Gwynedd.Mon@nwales-fireservice.org.uk |
| Conwy / Denbighshire | Conwy.Denbighshire@nwales-fireservice.org.uk |
| Wrexham / Flintshire | Flintshire.Wrexham@nwales-fireservice.org.uk |
| Mid & West Wales FRS | fpmp@mawwfire.gov.uk |
| South Wales FRS | SAFETYSOUTH@southwales-fire.gov.uk |
|  | C.C. m-bradford@southwales-fire.gov.uk |
|  | C.C. s-brock@southwales-fire.gov.uk |