Schedule 5 - Notification 

This page outlines the information that the Operator must provide. 

Units of measurement used in information supplied under Part A and B requirements shall be appropriate to the circumstances of the emission. Where appropriate, a comparison should be made of actual emissions and authorised emission limits.

If any information is considered commercially confidential, it should be separated from non-confidential information, supplied on a separate sheet and accompanied by an application for commercial confidentiality under the provisions of the EP Regulations.

Part A 
	Permit Number
	EPR/PR3733PC V008

	Name of Operator
	Biffa Waste Services Limited

	Location of Facility
	Trecatti Landfill Site

Fochriw Road

Merthyr Tydfil

Mid Glamorgan

CF48 4AB

	
	

	Time and date of the detection 
	10th October 2016 


	(a) Notification requirements for any malfunction, breakdown or failure of equipment or techniques, accident, or emission of a substance not controlled by an emission limit which has caused, is causing or may cause significant pollution

	To be notified within 24 hours of detection

	Date and Time of the event
	10th October 2016, 13:00hrs

	Reference or description of the location of the event 
	South West  Perimeter Point 14 on the attached map

	Description of where any release into the environment took place
	Trecatti landfill site, northern perimeter to the atmosphere. 

	Substances(s) potentially released
	Landfill Gas

	Best estimate of the quantity or rate of release of substances
	Unknown quantity - Peaked at 500ppm for a short time returning to a steady state below 40ppm recorded on the FID. 

	Measures taken, or intended to be taken, to stop any emission
	Issue tracked back to a split in a weld on the temporary capping, re-seal split in HDPE temp capping immediately undertaken by Celtic lining. 

	Description of the failure or accident.
	Split in extrusion weld of hdpe temp capping


	(b) Notification requirements for the breach of a limit

	To be notified within 24 hours of detection unless otherwise specified below

	Emission point reference/ source
	N/A

	Parameter(s)
	N/A

	Limit
	N/A

	Measured value and uncertainty
	N/A

	Date and time of monitoring
	N/A

	Measures taken, or intended to be taken, to stop the emission
	N/A


	Time periods for notification following detection of a breach of a limit

	Parameter
	Notification period

	N/A
	24 Hours


	(c) Notification requirements for the detection of any significant adverse environmental effect

	To be notified within 24 hours of detection

	Description of where the effect on the environment was detected
	N/A

	Substances(s) detected
	N/A

	Concentrations of substances detected
	N/A

	Date of monitoring/sampling
	N/A


Part B to be supplied as soon as practicable
	Any more accurate information on the matters for notification under Part A.
	Temp capping required re-sealing after coming away from the 2.5mm hdpe basal liner. Tear was repaired immediately on detection by Celtic lining. 

	Measures taken, or intended to be taken, to prevent a recurrence of the incident
	Continued weekly FID monitoring of the perimeter to identify areas of raised LFG emissions. Areas identified as having raised levels of LFG will trigger further in-depth monitoring to identify potential splits or tears in the temporary capping that may result in issues, these splits/tears will then be repaired where identified. 

	Measures taken, or intended to be taken, to rectify, limit or prevent any pollution of the environment which has been or may be caused by the emission
	No pollution to the environment occurred due to this reading.  

	The dates of any unauthorised emissions from the facility in the preceding 24 months.
	


	Name*
	Simon Milford

	Post
	Site Manager

	Signature
	Simon Milford

	Date
	12th October 2016 


* authorised to sign on behalf of the Operator.

