## Sheet1
RELEASES TO AIR
QUARTERLY RETURN | 2016 Quarter 4
MONTHLY MEAN, MAXIMUM DAILY MEAN AND ANNUAL PERCENTILE CONCENTRATIONS (a),(b),(c)
OPERATING MODE: | Auxiliary Firing
Operator: ENGIE Industrial Energy Services |  |  | Form: |  | IED CON 2 (Gas Turbines)
Location: | Dow Corning CHP |  | Version/date: |  | V.3.1 31 Dec 2015
Permit/Variation Number: | EPR/JP3632ZH
Year: | LCP:60 A2 (FB-001)
| NOx (mg/m3) |  |  | CO (mg/m3)
Month | Monthly Mean (d) | Max Daily Mean (d) | Part Load Max Daily Mean (e) | Monthly Mean (d) | Max Daily Mean (d) | Part Load Max Daily Mean (e)
January | 185.59 | 197.46 | 197.46 | 7.9 | 35.96 | 35.96
February | 189.6 | 199.59 | 199.59 | 3.56 | 12.88 | 12.88
March | 185.89 | 195.18 | 195.18 | 11.14 | 18.6 | 18.6
April | 0 | 0 | 0 | 0 | 0 | 0
May | 210.96 | 222.05 | 222.05 | 1.28 | 40.42 | 40.42
June | 207.3 | 214.1 | 214.1 | 1.71 | 6.33 | 6.33
July | 165.68 | 207.08 | 207.08 | 18.1 | 61.9 | 61.9
August | 190.12 | 202.93 | 202.93 | 2 | 2.6 | 2.6
September | 188 | 197.07 | 197.07 | 5.3 | 13.5 | 13.5
October | 197.95 | 205.31 | 205.31 | 4.2 | 8.4 | 8.4
November | 203.72 | 209.32 | 209.32 | 2.6 | 5.2 | 5.2
December | 203.72 | 209.35 | 209.35 | 2.5 | 5.5 | 5.5
Monthly ELV/Daily ELV (f) | 250 | 250 | 250 | 100 | 110 | 110
Annual 95th Percentile (g) | 250 |  |  | 200
Annual Percentile ELV (h)
NOTES:
(a) All data based on validated hourly average concentrations, excluding start-up and shut-down and periods of malfunction or breakdown of abatement equipment, at 15% O2, dry, 273.15K, 101.325 kPa
(b) Annual percentiles are submitted with the final return (Quarter 4)
(c) Extend report to cover the required number of LCP on each site and repeat report for each separately regulated Operating Mode as required, e.g., Combined Cycle, Open Cycle, Supplementary firing, Auxiliary firing
(d) Averages determined at loads in the range 70% < Load ≤ 100% ISO base load and above
(e) Averages determined at loads in the range MSUL* < Load ≤ 100% ISO base load and above (* For a 3 parameter approach, from the point of Start-Up to the point of Shut-down)
(f) Leave the Daily ELV blank if this is applied as a 95th percentile ELV within the Permit
(g) For each pollutant, report the Annual 95th percentile ELV for hourly averages in the first column and, if applicable, the Annual 95th percentile ELV for daily means in the second column
(h For each pollutant, report the Annual 95th percentile of hourly averages in the first column and, if applicable, the Annual 95th percentile of daily means in the second column
Signed on behalf of the Operator by: |  |  | ……………Hiram Mullan..…...…..…..
Date of return: |  |  | ……………..27/01/2017……………………..