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Checklist to be used when assessing Fire prevention and mitigation plans. 

Please note: 
this checklist has been produced to help you identify and record if the Fire Prevention and Mitigation Plan (FPMP) includes all the relevant information, in accordance with the guidance. This checklist is not a tick box exercise to enable you to determine if the plan is the suitable and each plan must be assessed and considered in terms of the risk of fire and how it will be prevented. 

If you are unsure whether the proposed measures are suitable, please check with your Senior Environment/ Permitting Officer.  In addition to this some useful information has been collated on the 01. FPMP query database saved here.
(Produced in accordance with guidance Version 2, August 2017)

Application number: 
Applicant: 
Facility Address: 
Date of assessment: 
Assessment carried out by: 
Save a copy in the site folder on the DMS
If the applicant doesn’t follow the minimum standards in the guidance, they must be able to justify why.  The measures they take instead must be equivalent or better.  They must include detailed assessments to satisfy us that the:
· likelihood of fire 
· impact from emissions during or after a fire on local people, critical infrastructure and the environment
· resources required by the Natural Resources Wales and other emergency responders during an incident
· post incident clean-up and remediation costs
are equivalent or less than would be incurred if the site followed the minimum standards in this regulatory guidance. 
Drafting notes to help complete this assessment record are included and are shown in red. These can be deleted as you work through your assessment.
FPMP Checklist summary
 
	Section 
	Compliant with guidance?
Yes / No / N/A
	Comments

	FPMP Summary
	
	

	Site Plan
	
	

	Common Causes of Fires and Preventative Measures
	
	

	Storage Times and self-combustion factors
	
	If yes, complete the relevant section below. If n/a, delete section of checklist

	Managing Waste Material Stacks and Separation Distances
	
	

	Baled Waste Storage 
	
	If yes, complete the relevant section below. If n/a, delete section of checklist

	Enclosing Stacks Using Bays and Walls 
	
	If yes, complete the relevant section below. If n/a, delete section of checklist

	Waste Stored Within a Building 
	
	If yes, complete the relevant section below. If n/a, delete section of checklist

	Waste Stored in Containers 
	
	If yes, complete the relevant section below. If n/a, delete section of checklist

	Layout of Waste Stacks on your Site 
	
	

	Seasonality and Waste Stack Management 
	
	If yes, complete the relevant section below. If n/a, delete section of checklist

	Monitoring and Turning of Stacks
	
	

	Fire Detection and Fire Suppression Systems 
	
	

	Firefighting Strategy 
	
	

	Water Supplies 
	
	

	Managing Water Run-off 
	
	

	Designated Quarantine Area 
	
	

	During and After an Incident 
	
	

	Reviewing and Monitoring your Fire Prevention & Mitigation Plan
	
	



FPMP Summary

	Does the fire prevention plan specify the following?  (the guidance states that it must)
	Yes/ No
	Comments

	A site plan
	YES
	Appendix 1

	the amount and type of waste received daily and how it is managed 	
	YES
	Refers back to wastes listed on permit and the waste acceptance procedure stipulated in the EMS.

	the total amount of waste and the types and forms (e.g. unprocessed, shredded, chipped, fines or baled) that are stored on site at any one time
	YES
	

	how each type of waste will be stored
	YES
	

	the maximum time each type of waste will be stored on site and how it will be managed
	NO
	No mention is made of storage times. 

	the location within the site where each type of waste will be stored
	YES
	Stated and refers to site plan. 

	the maximum size of any waste pile (in m3), stipulating the maximum length, width and depth
	YES
	Stated and refers to site plan. 

	the minimum separation (fire break) distance between waste piles or storage areas
	YES
	Stated and refers to site plan. 

	A clear area must be established around the perimeter of site; this can vary depending on the layout of your site and permitted stack sizes in accordance with the separation distances as illustrated in Table 2 (this must be available at all times and identified on your site plan
	YES
	Stated and refers to site plan. 

	the fire prevention techniques used, including management of hotspots (sign of potential self-combustion), monitoring, reporting, recording and actions
	YES
	Not applicable for this site, only techniques are staff training / diligence which has been mentioned. 

	techniques used to minimise the risk of fire spreading within the site or from the site
	YES
	Not applicable for this site, aside stack heights/separation distances. Only other techniques are staff training / diligence.

	the steps and procedures to be followed if a fire occurs on your site
	YES
	

	all combustion products and emissions (to air, land and water) from the fire and the emergency response (including the impact on people, critical infrastructure and the environment) and how they will be minimised. Operator needs to recognise the pollution impact of smoke and fire water and impact on environment and people. 
	YES
		

	Contact details of sensitive receptors within 1km of your site. To protect sensitive receptors, does the plan include measures that will be used to raise the alarm and to inform local residents, e.g. local school, nursing home etc. These measures will be site specific. Operator may need to check emergency planning procedures with Local Authority. 
	YES
	Yes, sensitive receptors have been discussed at great length and contact details listed. 

	how safe access to the site for fire and rescue services and other emergency responders is achieved
	YES
	





Site Plan 
(could consist of location plan, site plan and drainage plans on one or more plan)

	Does the site plan include the following:
The FPMP must include a site plan(s) drawn to scale showing:
	Yes/ No
	Comments

	layout of buildings
	YES
	

	any areas where hazardous materials are stored on site (location of gas cylinders, process areas, chemicals, piles of combustible materials, oil and fuel tanks)
	YES
	

	main access routes for fire engines and any alternative access
	YES
	

	access points around the site perimeter to assist firefighting – see table in guidance for typical FRS vehicle access requirements
	Partial
	The site is tightly confined, so access is largely limited to the main gate. However, some access may be gained over the fence from the Potters site. The FPMP includes the site drainage plan for Potters, so potential for access from here?


	hydrants and water supplies
	Partial
	There is one fire hydrant listed outside the site’s entrance, but no mention is made of any other water supplies 
· Instructions to close penstock valve, but no information on the volume of water this can store.
· Need to list/show the location of the fire extinguishers mentioned in the plan. 

	any watercourse, borehole or well located within or near the site
	n/a
	

	areas of natural and unmade ground
	YES
	No unmade ground listed on the site plan.

	the location of plant, protective clothing and pollution control equipment and materials
	n/a
	2

	drainage systems, foul and surface water drains, and their direction of flow and outfall points
	Partial
	No mention of surface water or foul drains, though does show the direction of surface water flow. Appendix includes drainage plan for the Potters site, but not Welsh Border Motor Spares itself. 

	the location of drain covers and any pollution control features such as drain closure valves and firewater containment systems
	Partial
	In the plan it describes shutting off the penstock valve, but does not state capacity of storage in this system. 


	location of “off- site” emergency information pack with site plan (as specified above)
	YES
	Site plan stored in box just inside the main gate and behind the main customer desk. 

	location of key receptors such as critical infrastructure, schools, hospitals, residential areas, workplaces, protected habitats and rivers within 1km of the site
	YES
	1

	Location of the quarantine area
	YES
	2

	compass rose showing north and the prevailing wind direction
	YES
	All

	Has the applicant included actions to be taken should a fire occur such as:
	Yes/ No
	Comments

	reducing the amount of firewater run-off generated - use sprays and fogs rather than jets
	NO
	

	recycling firewater if it’s not hazardous and it’s possible to reuse
	YES
	

	applying water to cool unburned material and other hazards, taking care to prevent this water causing or adding to water pollution and/or increasing air pollution
	NO
	

	separating unburned material from the fire using heavy plant
	NO
	

	separating burning material from the fire to quench it with hoses or in pools or tanks of water (this will reduce the amount of firewater produced)
	NO
	

	using soil, sand, crushed brick and/or gravel (if smoke is threatening local communities) to help suppress the fire, although you can only do this when:
	
	

	· groundwater vulnerability is low

	
	

	· agreed as a part of a firefighting strategy by the FRS and supported by NRW
	
	

	· contaminated material is removed and legally disposed of as soon as it is safe to do so
	
	

	To decide which of these options, or combinations of options, is appropriate the applicant must consider the following. Have they considered these?
	Yes/ No
	Comments

	scale and nature of the environmental hazards on site and the activities that take place on it
	YES
	

	risks posed to people, the environment and property
	n/a
	

	type of materials you store on site, the form they’re stored in and the length of time needed to extinguish a fire involving them
	YES
	

	availability of firewater containment facilities
	Partial
	See above, storage capacity for firewater not stated. 

	local topography, weather conditions and fire scenarios that could reasonably be expected on site
	YES
	


Common causes of fires and preventative measures
 
	The FPMP should consider where applicable the common causes of fire, some won’t apply, others need to be included
	Yes/ No
	Comments

	arson or vandalism
	YES
	

	Visitors & contractors
	n/a
	

	Ignition sources 
	YES
	

	self-combustion (e.g. due to chemical oxidation)
	YES
	

	plant or equipment failure
	YES
	

	discarded smoking materials
	YES
	

	hot works (e.g. welding or cutting)
	YES
	

	industrial heaters
	n/a
	

	Plant & hot exhausts
	YES
	

	damaged or exposed electrical cables
	YES
	

	Reaction between wastes
	n/a
	

	hot loads deposited at the site
	YES
	

	Build up loose combustible waste, dust and fluff
	n/a
	

	“Tramp” metal
	n/a
	

	Batteries within waste deposits
	n/a
	

	Batteries in ELVs
	Partial
	Confusing / contradictory wording?

	Cylinders stored at site
	n/a
	

	Leaks and spillages of oils and fuels
	NO
	



Storage times and self-combustion factors

	Self-combusting materials
	Yes/
No
	Comments

	Is the applicant storing materials at risk of self-combustion (see list in guidance)?  
	NO
	

	If yes, are they storing these in line with Table 1 – maximum storage times? 
	n/a
	

	If the applicant is storing materials at risk of self-combustion for longer than 3 months, has the applicant demonstrated additional measures they will take, including monitoring? Guidance states they MUST
	n/a
	

	Has the applicant considered adopting the following fire prevention principles? (Guidance states applicant should consider)
	
	

	reduce risk factors (e.g. exposed metal content, proportion of 'fines', mixing of materials and heat generated during treatment)

	n/a
	

	minimise stacks sizes (small stacks with appropriate separation are safer than one larger one)

	YES
	

	control moisture levels

	n/a
	

	demonstrate good stock rotation for all stored materials and show how this is monitored and implemented daily

	n/a
	

	store material in its largest form prior to processing e.g. do not undertake preparatory treatments such as size reduction of green waste unless you are intending on submitting the waste to the treatment process immediately

	n/a
	

	monitor and control sub-surface temperature and moisture content with a suitable thermal device (thermal probe/thermal camera) and ensure that this is capable of reaching all parts of a stack (if materials are stored in plastic wrapping you must demonstrate a sampling and testing protocol to ensure a representative number of bales (minimum 10%) are assessed during monitoring

	n/a
	

	routinely turn stacks
	n/a
	

	detect and control hotspots within stacks (Note: steam is a good indicator of self-heating)

	n/a
	

	define the maximum storage time of all materials on site and show how this will be monitored and controlled

	NO
	

	minimise external heating during hot weather by shading from direct sunlight
	n/a
	



Managing Waste Material Stacks and Separation Distances

	Guidance says MUST be used
	Yes/No
	Comments

	Are stack lengths and separation distances in line with Graph 1 for general wastes such as RDF, SRF (Refuse derived fuel/solid recovered fuel - various types of fuel derived from wastes using various treatment processes), wood, paper etc.
	n/a
	

	Are stack lengths and separation distances in line with Graph 2 for plastics and rubber wastes?
	n/a
	

	Graphs 1 and 2 assume a stack height of 4m, if stack sizes are significantly lower bespoke separation distances can be used – does this apply?
	n/a
	

	Has a competent fire engineer been used to calculate any bespoke separation distances?
	n/a
	

	Storage of whole end of life vehicles (ELVs)
Applicant MUST set out in the FPMP how they will store ELVs
	
	

	Is each vehicle accessible from at least one side allow a fire to be fought and so unburnt vehicles can be accessed and moved to prevent the fire spreading (These rules will limit any row to a depth of 2 vehicles.)
	YES
	

	If the applicant proposes to store vehicles one on top of another, or on racking, they should limit this to 3 vehicles high so the stack can remain stable during a fire. You should maintain a minimum separation distance between rows or blocks of vehicles in accordance with Table 2 (depending on the length of the rows)
	YES
	

	As part of the applicants’ waste stack management protocol they should consider adopting the following general fire prevention and mitigation principles:
	Yes/No
	

	manage all stacks to within the maximum sizes and minimum separation distances

	YES
	

	have availability to adequate water supplies or alternative firefighting methods at all times to fight a fire

	NO
	

	enable easy access for emergency vehicles around the whole site
	YES
	

	manage all stacks of materials that can self-combust and demonstrate suitable additional precautions if they are stored for more than 3 months
	n/a
	





Baled waste storage

	The guidance states the FPMP MUST show how they are reducing the risk of fire occurring in bales.
	Yes/ No
	Comments

	Does the applicant show how they are reducing the risk of fire occurring in bales?
	N/A
	

	In regards to baled waste storage, it is RECOMMENDED the FPMP show:
	
	

	what sampling and testing protocol you will use to make sure you assess a representative number of bales (minimum 10%) during monitoring
	N/A
	

	that you get representative temperature readings from the centre of the bales; and from bales within the centre of each stack pile
	N/A
	

	that you turn the bales to make sure the waste stays cold
	N/A
	

	If baled waste may exceed limits in Table 1, have additional measures, such as breaking and rewrapping bales been taken? Have additional fire risks that may be introduced from such measures been addressed e.g. sudden introduction of oxygen
	N/A
	

	What is the storage configuration of the bales? Has any fire risk from the configuration been addressed?
	N/A
	





Enclosing stacks using bays and walls

	Guidance states the bays and/or stacks SHOULD be able to provide the following
	Yes/ No
	Comments

	120 minutes’ fire resistance period
	N/A
	

	The guidance states that the FPMP SHOULD demonstrate:
	
	

	full and frequent stock rotation and how this will be monitored and recorded
	N/A
	

	protection from wind
	N/A
	

	how you intend to check temperature and moisture content of all the material within the bay so that the entire volume of the pile receives representative checks
	N/A
	

	t the construction of the walls in terms of how they offer a thermal barrier and enable cooling
	N/A
	

	how stock capacity will be managed and controlled
	N/A
	

	how you will ensure segregation of materials
	N/A
	

	how calculation of flame height and radiation has been taken into account in preventing the spread of fire between piles
	N/A
	

	prevention of brands or lighted material moving outside the bay walls
	N/A
	

	prevention of bridging across or around walls
	N/A
	

	how a ‘freeboard’ space at the top and sides of the walls will be physically retained at all times in accordance with the latest available guidance
	N/A
	

	the frequency and method of turning piles
	N/A
	

	how the quarantine area will be used and how materials will be moved during an incident
	N/A
	




Waste stored within a building

	If the applicant is storing waste in a building, the guidance states they SHOULD adopt the following principles at all times
	Yes/ No
	Comments

	Ensure waste stack sizes and separation distances are appropriate to the risk. Table 2 can be used as a starting point but not absolute guidance for internal storage.
General principles should be adopted:
	N/a
	

	Consider the use of fire walls/bunkers.
	n/a
	

	Separation between internally stored wastes and building walls, plant & other equipment within buildings will need to be considered. In general fires in internally stored wastes are far more likely to spread to buildings and plant than for externally stored wastes. As a result, your insurer is likely to place more emphasis on internal storage than external storage fire management. You should seek advice from your insurer to ensure that you have met any requirements for fire detection and fire suppression.
	n/a
	

	If you are storing wastes internally in large quantities, such as in warehousing, then you should seek competent advice on the precautions to be taken. These will depend on the type of building used, the types of waste being stored and what fire precautions are already in place. This is a specialised area, and the general standards applied to the warehousing of goods may not be appropriate to the internal storage of wastes.
	n/a
	

	If the building is heated this could affect the potential for self-heating of the waste and should be taken into account when assessing self-heating risks.
	n/a
	

	You must ensure that all escape routes, fire exits, alarm call points and fire extinguishers are kept clear and free from waste at all times
	n/a
	

	Ensure electrical equipment and heaters are kept free from waste, including dust and packaging materials.
	n/a
	

	Waste storage areas should be fire compartmented away from office areas.
	n/a
	

	Waste storage areas should have some means of clearing smoke from the building, such as openable skylights or roller shutter doors, to aid fire-fighting.
	n/a
	




Waste Stored in containers

	Has the applicant included the following (guidance states you must):
	Yes/ No
	Comments

	If you store waste in containers that can hold more than 1,100 litres, each one must be accessible so any fire inside it can be extinguished, for all other containers holding waste, the appropriate stack sizes apply as per Table 2
	n/a
	

	Guidance states the applicant SHOULD manage containers as follows:
	
	

	Shipping containers should be stacked no more than 2 containers high and secured with a lock outside of operational hours.
	n/a
	

	If you have a fire, you should be able to move containers as soon as is reasonably practicable in a safe manner to prevent the fire spreading. You should set out in your FPMP the procedures you will put in place to allow this to happen.
	n/a
	



Layout of waste stacks on site

	In addition to stack sizes, storage methods/types and appropriate separation distances, has the applicant taken into consideration the following factors?  (Guidance says these factors MAY need to be taken into account)
	Yes/No
	Comments

	Location of potential ignition sources on your site
	YES
	

	Location/s of occupied buildings and high-asset value equipment and plant
	YES
	

	Escape and evacuation routes around your site and within buildings must not be compromised by stack layout
	no
	No information given on location of emergency exits

	Location of flammable and/or hazardous substances kept on site, such as gas cylinder cages, diesel tanks, quarantine areas which may contain non-conforming wastes etc.
	YES
	

	Locations of on or off-site fire hydrants, other water supplies and fire-fighting equipment – you do not want to block access to these with your stack layout
	Partial
	One fire hydrant accessible just outside the front entrance to the site, however the plan provides little detail on access to water e.g. capacity of penstock valve system or sources of water. 

	Proximity and location/s of any infrastructure which may be affected by a fire, such as overhead power lines, major roads, rail lines etc.
	YES
	

	Proximity and location/s of any off-site, third party buildings which may be affected by a fire
	YES
	

	Permitted amounts of wastes, and types of waste, allowed on site
	YES
	

	Location of a ‘quarantine’ area, as appropriate to site specifics
	YES
	

	Operational practicalities such as movements of vehicles & designated routes
	no
	

	Stock rotation requirements, seasonality of supply/off-take etc.
	n/a
	

	The applicant should also consider
	
	

	the prevailing wind, where fire water will flow and the firefighting strategy that will be used.
	YES
	




Seasonality and waste stack management
 
	Has the applicant included the following (guidance states they SHOULD):
	Yes/ No
	Comments

	provide a technical assessment that shows you have confidence that your proposal will be viable in foreseeable market conditions – this should prove the suitability of materials, the resilience of the supply chain and end user outlets
	n/a
	

	If the materials on your site are subject to seasonal variation in demand and/or supply you should demonstrate how you intend to manage these variations. You should be able to demonstrate how you will follow the principle of “first in, first out” so that wastes are stored for no longer periods than indicated in Table 1.
	n/a
	






Monitoring and turning of stacks

	Has the applicant stated how they will achieve this and included the following? (Guidance states they should)
	Yes/ No
	Comments

	The staff must be trained to detect and manage hotspots. 
	n/a
	

	Piles are monitored regularly and temperature increases and changes in moisture content are minimised.  
	n/a
	

	The equipment they use to detect temperature and moisture content must be capable of operating at any depth throughout the pile.  Therefore, if they are proposing to have a stack 4m deep, their probe must be capable of operating the depth of the proposed stack.
	n/a
	

	They must explain what indicators they will use in relation to temperature and moisture content and the escalation of actions in relation to these indicators.
	n/a
	


Fire detection and fire suppression systems

	Has the applicant included the following (guidance states they SHOULD):
	Yes/ No
	Comments

	When deciding what type of system to install you need to take into account that:
· the fire and rescue service may not be able to enter the building during a fire
· a suppression system may not extinguish a fire, although it may prevent a fire spreading and then allow the fire to be fought effectively by the fire and rescue service
· the water supply to a fire system is reliable and adequate at all times
	NO
	

	Has the applicant considered fitting the following? (guidance states that they SHOULD consider)
	Yes/ No
	Comments

	automatic detection systems such as:
	NO
	

	· smoke and heat detectors including temperature probes
	NO
	

	· CCTV visual flame detection systems
	NO
	

	· spark, infrared and ultraviolet detection
	NO
	

	fire suppression systems such as:
	NO
	

	· sprinklers
	NO
	

	· manual open deluge system
	NO
	

	· deluge/water spray systems
	NO
	

	· water monitors/cannons/curtains
	NO
	



Firefighting Strategy

	Does the applicant have the following resources? (Guidance does not state whether they must have these or need to consider these)

	Yes/No
	Comments

	 (suitable) heavy mobile plant you have available that can be used to move waste around the site, for example loaders, excavators, material handlers
	NO
	

	the use of portable water carriers/bowsers can prove to be an essential mechanism to help extinguish fire effected waste
	NO
	

	adequately trained staff available
	NO
	

	available water supply
	NO
	

	finances available for additional resources
	NO
	

	Has the applicant described the firefighting techniques that would be employed using the said resources? (Guidance does not state whether they must have these or need to consider these)
	Yes/No
	Comments

	applying water to cool unburned material and other hazards
	n/a
	

	separating unburned material from the fire using appropriate heavy plant
	n/a
	

	separating burning material from the fire to quench it with hoses or in pools or tanks of water
	n/a
	

	suffocating the fire using soil, sand, crushed brick
or gravel. However, you can only do this if:
 Natural Resources Wales has agreed you can do this in the first instance, and
 you remove and dispose of contaminated material as soon as it is safe to do so
	n/a
	



Water supplies

	Have they considered the following? (Guidance states applicant MUST have adequate water supplies)
	Yes/ No
	Comments

	Has the applicant demonstrate that they will have sufficient water supplies available on their site to manage a worst-case scenario incident
	NO
	

	Has the applicant described what form their water supply is in? This could be water in storage tanks or lagoons on site, or access to hydrants or mains water supply for example.
	YES
	Access to one hydrant at the site entrance.

	Has the applicant referred to alternative water supplies such as a near-by river, canal, lake, lagoon etc. (in some rare cases wells can be used, but their capacity and recharge characteristics must be adequate)? These can be considered within their plan to supplement tanked or mains supplies however these alternative supplies need to be capable of being accessed promptly.
	NO
	




Managing fire water

The containment facilities and pollution equipment they need will depend on the size of the site, the amount of material they store and the firefighting strategy.  The CIRIA document 'Containment systems for the prevention of pollution (C736)' may help you identify the facilities and equipment you need for your site.

	The FPMP MUST set out how they will prevent fire water affecting the following receptors?
	Yes/ No
	Comments

	The local groundwater and surface water bodies
	yes
	

	Any well, spring or borehole within 50m used for the supply of water for human consumption, including private water supplies
	n/a
	

	Have they considered the following? (Guidance states applicant SHOULD be able to contain run-off
	Yes/ No
	Comments	

	Where is run off going to? If it is to sewer, a written agreement must be in the FPMP from the sewerage undertaker
	yes
	Run off drains towards the front entrance of the site and they have stated this would need to be bunded by the FRS. Site drain can be closed off by penstock valve and FPMP states to close this in the event of a fire. Water then would be tinkered off, with the contact details of these contractors provided in the plan. 

	How will they contain fire water? Has any secondary or tertiary containment been specified?
	yes
	As above.

	Are their measures suitable? This will depend on the size of the site, the amount of combustible material stored and the firefighting strategy
	yes
	Depending on the size of the fire – not sure on capacity of penstock valve system, though bunding would not retain a considerable amount. No other options readily available due to nature/size of site.

	Is there an environmental risk to the surrounding area? Groundwater/ watercourses/ habitats etc.
	yes
	The canal in Welshpool is a SAC and SSSI.





Designated quarantine area

	Has the applicant included the following (guidance states they SHOULD)
	Yes/ No
	Comments

	the location of this area and the volume of waste that it can hold
	Partial
	Location stated on the plan, however no detail provided on the volume of wastes that can be stored there.

	Is the quarantine area within the permitted boundary area of the site (guidance states it should)
	yes
	

	Does the quarantine area hold at least 50% of the volume of the largest stack,
	no
	

	Does the quarantine area have a separation distance of at least 6 metres around the quarantined waste (this can be decreased if concrete bunkers/walls will be used)
	yes
	


During and after an incident

	The FPMP must have contingency measures in place for dealing with issues during and after a fire (Guidance states they MUST)

	Yes/ No
	Comments

	diverting incoming wastes to alternative sites during a fire
	n/a
	

	having a plan for how you will notify those who may be affected by a fire, such as nearby residents and businesses

	yes
	

	contractors that might be used to assist with additional plant for firefighting techniques, removal of waste material, containment and removal of excess water run-off
	yes
	

	how you will clear and decontaminate the site
	partial
	Covered but not in great detail.

	the steps you must take before the site can become operational again
	partial
	Covered but not in great detail.



[bookmark: _GoBack]Reviewing and Monitoring your Fire Prevention & Mitigation Plan

	The guidance states that FPMP SHOULD be treated as a live document
	Yes/ No
	Comments

	Has the applicant described methods and procedures used to maintain compliance as a separate section within your Fire Prevention and Mitigation Plan?
	no
	

	Have they stated the circumstances that would warrant a review, these could include:
· Experiencing a fire incident. Following any fire, it is essential that your FPMP (and overall fire management measures) should be reviewed and improved as required to address any issues/concerns
· Additional combustible waste streams accepted on site.
· Increase waste volumes accepted.
· Development of site infrastructure – new buildings.
· Installation of new equipment or plant – baler/loading shovel/sort-line/trommel etc.
	partial
	Covered but not in great detail.

	Have they described the areas of the FPMP that would need updating because of said circumstances? (see the guidance for examples)
	partial
	Covered but not in great detail.




	




FPMP assessment checklist Version 2
Document owner – Improving Compliance Group March 2018

21

image1.jpeg
Cyfoeth
Naturiol
Cymru

Natural
Resources
Wales




