Permit Number: 	EPR/AB3092ZE			Operator: Bryn Power Limited

Facility:	AD Facility at Gelliargwellt Farm		Form Number: 	 Air1 / 21/01/16

# Reporting of emissions to air for the period from 20/01/16 to 19/01/17

| Emission Point | Substance / Parameter | Emission # Limit Value | Reference Period | Result [1] | Test Method [2] | Sample Date and Times [3] | Uncertainty [4] |
| --- | --- | --- | --- | --- | --- | --- | --- |
| A1 CHP Exhaust | Oxides of Nitrogen (NO and NO2 expressed as NO2) | 500mg/m3 | Hourly mean | 80.52 | BS EN 14792 | 9/3/17 15:42 to 16:41 | 2 |
|  | Carbon Monoxide | 1400mg/m3 | Hourly mean | 1163.39 | BS EN 15058 | 9/3/17 15:42 to 16:41 | 3 |
|  | Sulphur Dioxide | 350mg/m3 | Hourly mean | 115.45 | BS EN 14791 | 9/3/17 15:16 to 16:16 | 13 |
|  | VOC’s | 1000mg/m3 | Hourly mean | 1699.02 | BS EN 12619:1999 or 13526:2002 depending on concentration | 9/3/17 14:55 to 15:54 | 3 |
| CHP 2 Exhaust | Oxides of Nitrogen (NO and NO2 expressed as NO2) | 500mg/m3 | Hourly mean | 499.46 | BS EN 14792 | 9/3/17 13:09 to 14:08 | 2 |
|  | Carbon Monoxide | 1400mg/m3 | Hourly mean | 820.85 | BS EN 15058 | 9/3/17 13:09 to 14:08 | 3 |
|  | Sulphur Dioxide | 350mg/m3 | Hourly mean | 88.15 | BS EN 14791 | 9/3/17 12:59 to 13:59 | 13 |
|  | VOC’s | 1000mg/m3 | Hourly mean | 996.70 | BS EN 12619:1999 or 13526:2002 depending on concentration | 9/3/17 12:53 to 13:53 | 3 |
| A2 Flare Stack Note5 | Oxides of Nitrogen (NO and NO2 expressed as NO2) | 150mg/m3 | Hourly mean |  | BS EN 14792 |  |  |
|  | Total Volatile Organic Compounds (VOCs) | 10mg/m3 | Hourly mean |  | BS EN 12619:1999 or BS EN 13526:2002 |  |  |
|  | Carbon Monoxide | 50mg/m3 | Hourly mean |  | BS EN 15058 |  |  |

Signed …………………JCM………………………………………….  		Date……23/03/2017………………

(Authorised to sign as representative of Operator)                                                          NB The flare hasn’t run enough to require testing

Permit Number: 	EPR/AB3092ZE			Operator: Bryn Power Limited

Facility:	AD Facility at Gelliargwellt Farm		Form Number:	Performance1 / 21/01/16

# Reporting of other performance indicators for the period 20/01/2016 to 19/01/2017

| Parameter |  |  | Units |  |
| --- | --- | --- | --- | --- |
| Power output – Electricity |  | 4682.12 | MWh |  |
| Energy efficiency |  | 0.001951 | MWh/m3 biogas |  |
| Electrical energy exported to the grid |  | 1990.39 | MWh |  |
| Electrical energy drawn from the grid |  | 50.05 | MWh |  |
| Water usage |  | 260 | m3 |  |
| Operational time of emergency flare |  | 0.06 | % of operational time |  |
| Amount of biogas combusted in the CHPs unit per day NB calculated for both CHPs |  | 5714.4 | m3/day |  |

Operator’s comments :

Signed ………………………JCM…………………………………….  		Date……23/03/2017………..

(Authorised to sign as representative of Operator)