[bookmark: _Hlk506896081]Permit Number: 	EPR/AB3092ZE			Operator: Bryn Power Limited		

Facility:	AD Facility at Gelliargwellt Farm		Form Number: 	 Air1 / 21/01/16
Reporting of emissions to air for the period from 20/01/17 to 20/01/18 
	Emission
Point
	Substance /
Parameter
	Emission
Limit Value
	Reference Period
	Result [1]
	Test
Method [2]
	Sample
Date and Times [3]
	Uncertainty
[4]

	A1 CHP Exhaust 

Jenbacher

	Oxides of Nitrogen (NO and NO2 expressed as NO2)
	500mg/m3
	Hourly mean
	425
	BS EN 14792
	04/01/18
	21.8

	
	Carbon Monoxide
	1400mg/m3
	Hourly mean
	945
	BS EN 15058
	04/01/18
	47.8

	
	Sulphur Dioxide
	350mg/m3
	Hourly mean
	303
	BS EN 14791
	04/01/18
	23.9

	
	VOC’s
	1000mg/m3
	Hourly mean
	1002
	 BS EN 12619:1999 or 13526:2002 depending on concentration
	04/01/18
	78.7

	A2 Flare Stack Note5
	Oxides of Nitrogen (NO and NO2 expressed as NO2)
	150mg/m3
	Hourly mean
	n/a
	BS EN 14792
	n/a
	n/a

	
	Total Volatile Organic Compounds (VOCs)
	10mg/m3
	Hourly mean
	n/a
	BS EN 12619:1999 or BS EN 13526:2002
	n/a
	n/a

	
	Carbon Monoxide
	50mg/m3
	Hourly mean
	n/a
	BS EN 15058
	n/a
	n/a



[1] The result given is the maximum value (or the minimum value in the case of a limit that is expressed as a minimum) obtained during the reporting period, expressed in the same terms as the emission limit value. Where the emission limit value is expressed as a range, the result is given as the ‘minimum – maximum’ measured values.
[2] Where an internationally recognised standard test method is used the reference number is given. Where another method that has been formally agreed with Natural Resources Wales is used, then the appropriate identifier is given. In other cases the principal technique is stated, for example gas chromatography.
[3] For non-continuous measurements the date and time of the sample that produced the result is given. For continuous measurements the percentage of the process operating time covered by the result is given.   
[4] The uncertainty associated with the quoted result at the 95% confidence interval, unless otherwise stated.
[5] Monitoring of flare emissions is only necessary when the flare operated in excess of 10% of the time



Signed …………………………JCP………………………………….  		Date  20.02.2018.   	
	(Authorised to sign as representative of Operator)

Permit Number: 	EPR/AB3092ZE			Operator: Bryn Power Limited		

Facility:	AD Facility at Gelliargwellt Farm		Form Number: 	 Air1 / 21/01/16
Reporting of emissions to air for the period from 20.01.17 to 20.01.18
	Emission
Point
	Substance /
Parameter
	Emission
Limit Value
	Reference Period
	Result [1]
	Test
Method [2]
	Sample
Date and Times [3]
	Uncertainty
[4]

	A2 CHP Exhaust 

Edina 

	Oxides of Nitrogen (NO and NO2 expressed as NO2)
	500mg/m3
	Hourly mean
	428
	BS EN 14792
	04/01/18
	22.5

	
	Carbon Monoxide
	1400mg/m3
	Hourly mean
	936
	BS EN 15058
	04/01/18
	45.6

	
	Sulphur Dioxide
	350mg/m3
	Hourly mean
	320
	BS EN 14791
	04/01/18
	26.5

	
	VOC’s
	1000mg/m3
	Hourly mean
	899
	 BS EN 12619:1999 or 13526:2002 depending on concentration
	04/01/18
	65.1



[5] The result given is the maximum value (or the minimum value in the case of a limit that is expressed as a minimum) obtained during the reporting period, expressed in the same terms as the emission limit value. Where the emission limit value is expressed as a range, the result is given as the ‘minimum – maximum’ measured values.
[6] Where an internationally recognised standard test method is used the reference number is given. Where another method that has been formally agreed with Natural Resources Wales is used, then the appropriate identifier is given. In other cases the principal technique is stated, for example gas chromatography.
[7] For non-continuous measurements the date and time of the sample that produced the result is given. For continuous measurements the percentage of the process operating time covered by the result is given.   
[8] The uncertainty associated with the quoted result at the 95% confidence interval, unless otherwise stated.
[5] Monitoring of flare emissions is only necessary when the flare operated in excess of 10% of the time



[bookmark: _GoBack]Signed ………JCP…………………………….  		Date…20.02.18  
